## Ranking Region
Region | Total Interruption | Total Faults | Total Outage Duration | SAIDI | ASAI | ASIFI | Fault Clearance Index | Ranking SAIDI | Ranking ASAI | Ranking ASIFI | Ranking FCI | Total Points | Overal Ranking
Kano Central | 141 | 132 | #VALUE! | #VALUE! | #VALUE! | 1.5393 | 0.68939 | #VALUE! | #VALUE! | 8 | 3 | #VALUE! | #VALUE!
Kano Industrial | 81 | 75 | #VALUE! | #VALUE! | #VALUE! | 1.6624 | 0.77333 | #VALUE! | #VALUE! | 9 | 1 | #VALUE! | #VALUE!
Kano East | 140 | 134 | -447746.2688 | -5.0923 | 597.995 | 1.9287 | 0.56716 | #VALUE! | #VALUE! | 10 | 5 | #VALUE! | #VALUE!
Kano West | 77 | 74 | 1900-01-15 16:30 | 0.092625 | 0.96728 | 1.0366 | 0.7027 | #VALUE! | #VALUE! | 6 | 2 | #VALUE! | #VALUE!
Katsina North | 46 | 46 | -87357.3951 | -1.4632 | 112.9967 | 0.29074 | 0.54348 | #VALUE! | #VALUE! | 2 | 6 | #VALUE! | #VALUE!
Katsina Central | 18 | 18 | -358220.0375 | -2.5351 | 1086.5153 | 0.38598 | 0.33333 | #VALUE! | #VALUE! | 3 | 8 | #VALUE! | #VALUE!
Katsina South | 27 | 27 | -403046.4007 | -2.5083 | 896.6587 | 0.25204 | 0.25926 | #VALUE! | #VALUE! | 1 | 9 | #VALUE! | #VALUE!
Jigawa North | 32 | 32 | -108.4715 | -0.14026 | 1.241 | 0.50754 | 0.1875 | #VALUE! | #VALUE! | 4 | 10 | #VALUE! | #VALUE!
Jigawa South | 50 | 50 | -223773.484 | -2.1364 | 679.1015 | 0.85505 | 0.52 | #VALUE! | #VALUE! | 5 | 7 | #VALUE! | #VALUE!
Kano North | 91 | 89 | 6422724.2576 | 0.11301 | -8919.4504 | 1.0703 | 0.58427 | #VALUE! | #VALUE! | 7 | 4 | #VALUE! | #VALUE!

## Ranking TSP
Sr. No. | Region | TSP | Total Interruptions | Total Faults | TOTAL NUMBERS OF FEEDERS/TSP | Tripping Due to Fault | Planned Shutdown | Substation Fault | Outage Surrender within Approved Duration | Total Outage Duration | Total Hours Available for Service | Days in the Month | Total Faults Cleared within Specified Time | Total PM Cleared within Specified Time | Average Interupption | Avg. Duration Per Tripping | SAIDI | ASIFI | ASAI | FCI | Ranking SAIDI | Ranking ASIFI | Ranking ASAI | Ranking FCI | Total Points | Overal Ranking
1 | Kano Central | Bompai | 61 | 58 | 8 | 58 | 3 | 0 | 0 | #VALUE! | #VALUE! | 30 | 45 | 0 | 7.625 | #VALUE! | #VALUE! | 2.5444 | #VALUE! | 0.77586 | #VALUE! | 26 | #VALUE! | 7 | #VALUE! | #VALUE!
2 | Kano North | IDH | 11 | 11 | 5 | 9 | 0 | 0 | 0 | 0.85903 | 1900-05-28 03:23 | 30 | 6 | 0 | 2.2 | 1:52 | 0.019212 | 0.25217 | 99.43% | 0.54545 | #VALUE! | 5 | #VALUE! | 15 | #VALUE! | #VALUE!
3 | Kano North | Kano City | 31 | 31 | 10 | 30 | 0 | 0 | 0 | -44836.8528 | 2023-07-29 20:28 | 30 | 18 | 0 | 3.1 | -1446.3501 | -10.2268 | 0.57147 | 15046% | 0.58065 | #VALUE! | 11 | #VALUE! | 14 | #VALUE! | #VALUE!
4 | Kano Central | Kedco HQ | 40 | 36 | 5 | 36 | 4 | 0 | 2 | -44809.4042 | 2023-02-02 09:42 | 30 | 28 | 2 | 8 | -1120.2351 | -5.787 | 1.2817 | 29973% | 0.77778 | #VALUE! | 20 | #VALUE! | 5 | #VALUE! | #VALUE!
5 | Kano North | Rijiyar Zaki | 49 | 47 | 9 | 41 | 2 | 0 | 1 | 6467560.2514 | -6467290.2514 | 30 | 28 | 1 | 5.4444 | 131991.0255 | 0.040847 | 2.1005 | -2395293% | 0.59574 | #VALUE! | 25 | #VALUE! | 13 | #VALUE! | #VALUE!
6 | Kano Central | Sabon Gari | 26 | 25 | 10 | 22 | 1 | 0 | 1 | 1900-01-07 16:11 | 1900-10-17 07:49 | 30 | 13 | 1 | 2.6 | 8:00 | 0.072372 | 1.05 | 97.11% | 0.52 | #VALUE! | 17 | #VALUE! | 18 | #VALUE! | #VALUE!
7 | Kano Industrial | Akth | 28 | 26 | 6 | 26 | 2 | 0 | 1 | #VALUE! | #VALUE! | 30 | 23 | 1 | 4.6667 | #VALUE! | #VALUE! | 3.7139 | #VALUE! | 0.88462 | #VALUE! | 28 | #VALUE! | 1 | #VALUE! | #VALUE!
8 | Kano Industrial | Zoo Road | 21 | 20 | 5 | 18 | 1 | 0 | 1 | 1900-01-02 02:45 | 1900-05-25 21:15 | 30 | 16 | 1 | 4.2 | 3:34 | 0.17748 | 1.9417 | 97.92% | 0.8 | #VALUE! | 23 | #VALUE! | 2 | #VALUE! | #VALUE!
9 | Kano Industrial | Sharada | 22 | 19 | 7 | 18 | 3 | 0 | 2 | -89565.6285 | 2145-10-16 15:05 | 30 | 13 | 2 | 3.1429 | -4071.1649 | -10.276 | 1.0258 | 42750% | 0.68421 | #VALUE! | 16 | #VALUE! | 9 | #VALUE! | #VALUE!
10 | Kano Industrial | Dorayi | 10 | 10 | 5 | 9 | 0 | 0 | 0 | -44779.7778 | 2023-01-03 18:40 | 30 | 6 | 0 | 2 | -4477.9778 | -2.99 | 0.59185 | 29953% | 0.6 | #VALUE! | 12 | #VALUE! | 12 | #VALUE! | #VALUE!
11 | Kano East | Hotoro | 42 | 39 | 9 | 31 | 3 | 0 | 3 | -89502.0597 | 2145-10-13 01:26 | 30 | 24 | 3 | 4.6667 | -2131.0014 | -2.6438 | 2.0263 | 33249% | 0.61538 | #VALUE! | 24 | #VALUE! | 11 | #VALUE! | #VALUE!
12 | Kano East | Kawaji | 51 | 48 | 7 | 48 | 3 | 0 | 1 | -223906.0688 | 224146.0688 | 30 | 30 | 1 | 6.375 | -4390.3151 | -8.0916 | 1.6316 | 93394% | 0.625 | #VALUE! | 22 | #VALUE! | 10 | #VALUE! | #VALUE!
13 | Kano East | Wudil | 47 | 47 | 5 | 44 | 0 | 0 | 0 | -134338.1403 | 2268-04-17 03:22 | 30 | 22 | 0 | 7.8333 | -2858.2583 | -1.7302 | 2.7026 | 74732% | 0.46809 | #VALUE! | 27 | #VALUE! | 19 | #VALUE! | #VALUE!
14 | Kano West | Kwanar Dangora | 33 | 33 | 5 | 33 | 0 | 0 | 0 | 1900-01-04 08:01 | 1900-05-23 15:59 | 30 | 26 | 0 | 6.6 | 3:53 | 0.098237 | 1.27 | 96.44% | 0.78788 | #VALUE! | 19 | #VALUE! | 3 | #VALUE! | #VALUE!
15 | Kano West | Maikalwa | 26 | 23 | 7 | 21 | 3 | 0 | 0 | 1900-01-06 00:01 | 1900-07-20 23:59 | 30 | 12 | 0 | 3.7143 | 6:28 | 0.10346 | 0.82263 | 96.67% | 0.52174 | #VALUE! | 15 | #VALUE! | 17 | #VALUE! | #VALUE!
16 | Kano West | Panshekara | 18 | 18 | 5 | 17 | 0 | 0 | 0 | 1900-01-03 08:28 | 1900-05-24 15:32 | 30 | 14 | 0 | 3.6 | 5:48 | 0.071952 | 1.0943 | 97.1% | 0.77778 | #VALUE! | 18 | #VALUE! | 5 | #VALUE! | #VALUE!
17 | Katsina North | Daura | 17 | 17 | 5 | 17 | 0 | 0 | 0 | -44776.2396 | 2022-12-31 05:45 | 30 | 7 | 0 | 3.4 | -2633.8964 | -2.392 | 0.45498 | 29951% | 0.41176 | #VALUE! | 9 | #VALUE! | 21 | #VALUE! | #VALUE!
18 | Katsina North | Katsina City | 12 | 12 | 9 | 12 | 0 | 0 | 0 | 1899-12-31 11:13 | 1900-10-24 12:47 | 30 | 9 | 0 | 1.2 | 2:56 | 0.017255 | 0.38644 | 99.51% | 0.75 | #VALUE! | 8 | #VALUE! | 8 | #VALUE! | #VALUE!
19 | Katsina North | Katsina Urban | 17 | 17 | 9 | 16 | 0 | 0 | 0 | -42582.6229 | 2017-06-26 14:57 | 30 | 9 | 0 | 1.5455 | -2504.8602 | -0.5011 | 0.19912 | 13004% | 0.52941 | #VALUE! | 2 | #VALUE! | 16 | #VALUE! | #VALUE!
20 | Katsina Central | Dutsenma | 3 | 3 | 1 | 3 | 0 | 0 | 0 | -89555.684 | 2145-05-09 16:25 | 30 | 0 | 0 | 1.5 | -29851.8947 | -1.1991 | 0.082663 | 149359% | 0 | #VALUE! | 1 | #VALUE! | 28 | #VALUE! | #VALUE!
21 | Katsina Central | Kankia | 15 | 15 | 9 | 15 | 0 | 0 | 0 | -268664.3535 | 268934.3535 | 30 | 6 | 0 | 1.6667 | -17910.9569 | -2.9803 | 0.529 | 99605% | 0.4 | #VALUE! | 10 | #VALUE! | 22 | #VALUE! | #VALUE!
22 | Katsina South | Funtua | 14 | 14 | 11 | 14 | 0 | 0 | 0 | -223872.6208 | 224202.6208 | 30 | 5 | 0 | 1.2727 | -15990.9015 | -3.0559 | 0.26628 | 67940% | 0.35714 | #VALUE! | 6 | #VALUE! | 24 | #VALUE! | #VALUE!
23 | Katsina South | Malumfashi | 13 | 13 | 4 | 13 | 0 | 0 | 0 | -179173.7799 | 2390-11-19 18:43 | 30 | 2 | 0 | 3.25 | -13782.5985 | -1.8236 | 0.23005 | 149411% | 0.15385 | #VALUE! | 3 | #VALUE! | 27 | #VALUE! | #VALUE!
24 | Jigawa North | Hadejia | 23 | 23 | 9 | 22 | 0 | 0 | 0 | -52.2333 | 1900-11-17 05:36 | 30 | 4 | 0 | 2.5556 | -2.271 | -0.085635 | 0.65403 | 119.3% | 0.17391 | #VALUE! | 13 | #VALUE! | 26 | #VALUE! | #VALUE!
25 | Jigawa North | Gumel | 9 | 9 | 4 | 7 | 0 | 0 | 0 | -56.2382 | 1900-08-23 05:43 | 30 | 2 | 0 | 1.5 | -6.2487 | -0.21476 | 0.23209 | 131.2% | 0.22222 | #VALUE! | 4 | #VALUE! | 25 | #VALUE! | #VALUE!
26 | Jigawa South | Birnin Kudu | 14 | 14 | 3 | 14 | 0 | 0 | 0 | 1900-01-01 09:17 | 1900-03-27 14:43 | 30 | 11 | 0 | 4.6667 | 4:06 | 0.076583 | 1.3316 | 97.35% | 0.78571 | #VALUE! | 21 | #VALUE! | 4 | #VALUE! | #VALUE!
27 | Jigawa South | Dutse | 36 | 36 | 7 | 35 | 0 | 0 | 0 | -223775.8708 | 224015.8708 | 30 | 15 | 0 | 4.5 | -6215.9964 | -2.1373 | 0.71764 | 93340% | 0.41667 | #VALUE! | 14 | #VALUE! | 20 | #VALUE! | #VALUE!
28 | Kano Central | Badawa | 14 | 13 | 5 | 11 | 1 | 0 | 1 | -44780.4757 | 2023-01-04 11:25 | 30 | 5 | 1 | 2.8 | -3198.6054 | -1.3953 | 0.30592 | 29954% | 0.38462 | #VALUE! | 7 | #VALUE! | 23 | #VALUE! | #VALUE!
Formulas:
Total Hours Available for Service = SUMIF(Main!C:C,Table1[[#This Row],[TSP]],Main!S:S)

## Main
Region | Transmission/ Injection Station | TSP | Feeder | Type of Feeder | Total Interrruption | O/C Fault | E/F Fault | O/C & E/F Fault | NO RI | Transients | No Discovery on Patrols | Patrols with Discoveries | Outage Duration of Fault | Duration of Planned Outage | Duration of Planned Construction Activity | Duration of S/S Fault | Total Outage Duration | Available Hours for Service | Total Hours in Service | Tripping due to Line fault | Total Faults | Tripping due to S/S fault | Planned shutdown for construction activity | Planned shutdown for O&M activity | Shutdown on Emergency | Tripped due to under-frequency | No. of Outage Surrender within Duration | No. of Fault Cleared in Specified Time | No. of PM Done within Approved Time | Load Interrupted (MW) | Load at Restoration | Unrestored Load | Sum of Outage Duration & Load Interupption | Load Interrupted (KVA) | FEEDER BAND
KANO INDUSTRIAL | KUMBOTSO | SHARADA | 33KV DANGOTE | URBAN | 13 | 7 | 2 | 3 | 0 | 5 | 3 | 4 | -44782.5556 | 0 | 0 | 0 | -44782.5556 | 2022-09-08 13:20 | 1900-01-25 22:00 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162.8 | 0 | 162.8 | -761312.5356 | 191529.4118 | A
KANO INDUSTRIAL | KUMBOTSO | ZOO ROAD | 33KV ANGELS | URBAN | 6 | 3 | 3 | 0 | 0 | 2 | 2 | 2 | 0.63056 | 0 | 0 | 0 | 0.63056 | 1900-01-28 08:52 | 1900-01-27 19:00 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 55.5 | 0 | 55.5 | 5.7026 | 65294.1176 | A
KANO INDUSTRIAL | KUMBOTSO | SHARADA | 33KV BATA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO INDUSTRIAL | KUMBOTSO | DORAYI | 33KV ATM | URBAN | 2 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0.31875 | 0 | 0 | 0 | 0.31875 | 1900-01-28 16:21 | 1900-01-26 18:35 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 7.6 | 0 | 7.6 | 1.3078 | 8941.1765 | A
KANO INDUSTRIAL | KUMBOTSO | AKTH | 33KV SPANISH 1 | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-26 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO INDUSTRIAL | KUMBOTSO | ZOO ROAD | 33KV SPANISH 2 | URBAN | 7 | 6 | 1 | 0 | 0 | 4 | 2 | 1 | 0.89653 | 0 | 0 | 0 | 0.89653 | 1900-01-28 02:29 | 1900-01-24 20:28 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 130.3 | 0 | 130.3 | 16.8564 | 153294.1176 | A
KANO INDUSTRIAL | DANAGUNDI | AKTH | 33KV ZARIA ROAD | URBAN | 18 | 13 | 1 | 3 | 0 | 8 | 4 | 5 | 0.95278 | 0.10764 | 0 | 0 | 1899-12-31 01:27 | 1900-01-27 22:33 | 1900-01-21 15:58 | 17 | 17 | 0 | 0 | 1 | 0 | 0 | 1 | 16 | 1 | 248.4 | 0 | 248.4 | 18.6338 | 292235.2941 | A
KANO CENTRAL | DANAGUNDI | BADAWA | 33KV CLUB | URBAN | 4 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0.15764 | 0.20764 | 0 | 0 | 1899-12-31 01:11 | 1900-01-27 22:49 | 1900-01-21 09:12 | 1 | 3 | 0 | 0 | 1 | 2 | 0 | 1 | 2 | 1 | 12.1 | 0 | 12.1 | 2.2324 | 14235.2941 | A
KANO CENTRAL | DANAGUNDI | KEDCO HQ | 33KV CBN | URBAN | 18 | 7 | 8 | 2 | 0 | 4 | 9 | 3 | -44872.2632 | 0.031944 | 0 | 0 | -44872.2313 | 2022-12-07 05:33 | 1900-01-24 18:43 | 16 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 14 | 0 | 109 | 0 | 109 | -260365.9565 | 128235.2941 | A
KANO NORTH | DANAGUNDI | RIJIYAR ZAKI | 33KV BUK | URBAN | 14 | 3 | 1 | 8 | 0 | 1 | 10 | 1 | 6601899.709 | 0 | 0 | 0 | 6601899.7424 | -6601869.7424 | 1900-01-13 10:34 | 12 | 14 | 0 | 0 | 0 | 2 | 0 | 0 | 12 | 0 | 124.6 | 0 | 124.6 | -76125.3456 | 146588.2353 | A
KANO NORTH | DANAGUNDI | KANO CITY | 33KV KURNA | URBAN | 15 | 1 | 5 | 8 | 0 | 1 | 9 | 4 | -44841.0646 | 0 | 0 | 0 | -44840.6229 | 2022-11-05 14:57 | 1900-01-14 14:20 | 14 | 15 | 0 | 0 | 0 | 1 | 0 | 0 | 9 | 0 | 99.2 | 0 | 99.2 | -461611.5172 | 116705.8824 | A
KANO NORTH | DANAGUNDI/BUKAVU | RIJIYAR ZAKI | 33KV DAWANAU | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | -44784.4556 | 0 | 0 | 0 | -44784.4556 | 2022-09-10 10:56 | 1900-01-01 10:19 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0.7 | -31349.1189 | 823.5294 | E
KANO NORTH | DANAGUNDI | KANO CITY | 33KV DAN AGUNDI 1 | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-20 07:23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO NORTH | DANAGUNDI | KANO CITY | 33KV DAN AGUNDI 2 | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-18 09:24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO NORTH | KUMBOTSO | RIJIYAR ZAKI | 33KV RIJIYAR ZAKI | URBAN | 14 | 3 | 4 | 4 | 0 | 2 | 8 | 3 | 1899-12-31 02:12 | 0.35069 | 0 | 0 | 1899-12-31 12:06 | 1900-01-27 11:54 | 1900-01-11 17:30 | 11 | 13 | 0 | 0 | 1 | 2 | 0 | 0 | 13 | 0 | 159.3 | 0 | 159.3 | 15.1563 | 187411.7647 | A
KANO CENTRAL | DAKATA | SABON GARI | 33KV IDH | URBAN | 13 | 4 | 4 | 2 | 0 | 3 | 7 | 1 | 1899-12-31 10:44 | 0.067361 | 0 | 0 | 1899-12-31 13:59 | 1900-01-27 10:01 | 1900-01-17 15:26 | 10 | 12 | 0 | 0 | 1 | 2 | 0 | 1 | 9 | 1 | 131.3 | 0 | 131.3 | 14.8203 | 154470.5882 | A
KANO CENTRAL | DAKATA | BOMPAI | 33KV FLOUR MILLS | URBAN | 22 | 15 | 3 | 3 | 0 | 14 | 4 | 3 | 0.027778 | 0.034028 | 0 | 0 | 0.061806 | 1900-01-28 22:31 | 1900-01-24 10:14 | 21 | 21 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 315.4 | 0 | 315.4 | -2.3899 | 371058.8235 | A
KANO CENTRAL | DAKATA | BOMPAI | 33KV MTN | URBAN | 19 | 10 | 3 | 5 | 0 | 9 | 3 | 6 | 1899-12-31 12:01 | 0.038889 | 0 | 0 | 1899-12-31 12:57 | 1900-01-27 11:03 | 1900-01-22 00:43 | 18 | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 14 | 0 | 193.2 | 0 | 193.2 | 14.1801 | 227294.1176 | A
KANO CENTRAL | DAKATA | BOMPAI | 33KV SMALL SCALE | URBAN | 8 | 2 | 2 | 4 | 0 | 2 | 2 | 2 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | 1900-01-12 23:40 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 55.8 | 0 | 55.8 | #VALUE! | 65647.0588 | A
KANO EAST | DAKATA/SMALL SCALE | KAWAJI | 33KV GEZAWA | RURAL | 12 | 0 | 2 | 10 | 0 | 0 | 11 | 1 | 1900-01-01 01:38 | 0 | 0 | 0 | 1900-01-01 01:38 | 1900-01-26 22:22 | 1900-01-07 23:59 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 32.1 | 0 | 32.1 | 4.6886 | 37764.7059 | E
KANO EAST | DAKATA | KAWAJI | 33KV GASKIYA | URBAN | 22 | 7 | 6 | 8 | 0 | 5 | 10 | 2 | -179132.0021 | 0.25417 | 0 | 0 | -179131.7479 | 2390-07-10 17:57 | 1900-01-19 11:17 | 21 | 21 | 0 | 0 | 1 | 0 | 0 | 1 | 14 | 1 | 201.4 | 0 | 201.4 | -1809229.665 | 236941.1765 | A
KANO EAST | DAKATA | KAWAJI | 33KV JODA | URBAN | 3 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | -44780.9417 | 0 | 0 | 0 | -44780.9417 | 2022-09-06 22:36 | 1900-01-22 13:00 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.3 | 0 | 0.3 | -4478.0942 | 352.9412
KANO EAST | DAKATA | HOTORO | 33KV NNPC | URBAN | 20 | 5 | 5 | 6 | 0 | 4 | 10 | 1 | 1899-12-31 05:41 | -44783.4243 | 0 | 0 | -44782.1146 | 2022-09-08 02:45 | 1900-01-17 06:18 | 16 | 17 | 0 | 0 | 3 | 1 | 0 | 3 | 14 | 3 | 133 | 0 | 133 | -147776.3865 | 156470.5882 | A
KANO EAST | DAKATA | HOTORO | 33KV LADANAI | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-17 07:33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANO EAST | DAKATA/MARIRI | WUDIL | 33KV MAKOLE | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-14 07:26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO EAST | WUDIL TS | WUDIL | 33KV WUDIL | URBAN | 8 | 3 | 5 | 0 | 0 | 2 | 2 | 4 | -44781.2701 | 0 | 0 | 0 | -44781.2701 | 2022-09-07 06:29 | 1900-01-24 11:56 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 16.2 | 0 | 16.2 | -111953.6328 | 19058.8235 | A
KANO EAST | WUDIL TS | WUDIL | 33KV GANO | URBAN | 14 | 1 | 9 | 0 | 0 | 1 | 7 | 4 | -44783.05 | 0 | 0 | 0 | -44782.4264 | 2022-09-08 10:14 | 1900-01-15 07:16 | 11 | 14 | 0 | 0 | 0 | 3 | 0 | 0 | 8 | 0 | 68.8 | 0 | 68.8 | -22379.1527 | 80941.1765 | C
KANO EAST | WUDIL TS | WUDIL | 33KV GARKO | RURAL | 16 | 0 | 14 | 1 | 0 | 0 | 8 | 7 | -44779.9521 | 0 | 0 | 0 | -44779.9521 | 2022-09-05 22:51 | 1900-01-07 11:00 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 33.7 | 0 | 33.7 | -98516.5781 | 39647.0588 | E
KANO EAST | WUDIL/WUDIL | WUDIL | 33KV GAYA | RURAL | 8 | 3 | 5 | 0 | 0 | 0 | 6 | 2 | 1900-01-04 03:23 | 0 | 0 | 0 | 1900-01-04 03:23 | 1900-01-23 20:37 | 1900-01-06 08:15 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 8.5 | 0 | 8.5 | 5.6032 | 10000 | E
JIGAWA SOUTH | DUTSE | DUTSE | 33KV SUMAILA | RURAL | 14 | 0 | 12 | 1 | 0 | 0 | 11 | 1 | -89500.2403 | 0 | 0 | 0 | -89500.2403 | 2145-02-13 05:46 | 1900-01-13 04:56 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 23.1 | 0 | 23.1 | -187934.0036 | 27176.4706 | D
KANO WEST | KUMBOTSO | MAIKALWA | 33KV BAGAUDA | URBAN | 23 | 6 | 15 | 0 | 0 | 5 | 12 | 4 | 1900-01-03 20:00 | 0.475 | 0 | 0 | 1900-01-04 19:52 | 1900-01-23 04:08 | 1900-01-11 13:00 | 20 | 21 | 0 | 0 | 2 | 0 | 0 | 0 | 11 | 0 | 65.7 | 0 | 65.7 | 18.2822 | 77294.1176 | D
KANO WEST | DANAGUNDI/ZARIA RD | MAIKALWA | 33KV DAWAKI | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34097 | 0 | 0 | 0.34097 | 1900-01-28 15:49 | 1900-01-22 07:39 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 3.2 | 1.0911 | 3764.7059
KANO WEST | DANGORA | KWANAR DANGORA | 33KV LAW SCHOOL | RURAL | 12 | 2 | 7 | 3 | 0 | 1 | 11 | 0 | 1899-12-31 18:04 | 0 | 0 | 0 | 1899-12-31 18:04 | 1900-01-27 05:56 | 1900-01-18 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 31.1 | 0 | 31.1 | 4.7012 | 36588.2353 | D
KANO WEST | DANGORA | KWANAR DANGORA | 33KV KARAYE | RURAL | 11 | 1 | 7 | 3 | 0 | 0 | 11 | 0 | 0.77222 | 0 | 0 | 0 | 0.77222 | 1900-01-28 05:28 | 1900-01-21 19:00 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36.3 | 0 | 36.3 | 3.2819 | 42705.8824 | E
KANO WEST | DANGORA | KWANAR DANGORA | 33KV FALGORE | RURAL | 10 | 1 | 8 | 1 | 0 | 1 | 7 | 2 | 1900-01-01 19:25 | 0 | 0 | 0 | 1900-01-01 19:25 | 1900-01-26 04:35 | 1900-01-21 14:00 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 21.3903 | 0 | 21.3903 | 6.2284 | 25165.0327 | E
KANO WEST | TAMBURAWA | PANSHEKARA | 33KV KWANKWASO | RURAL | 15 | 1 | 7 | 7 | 0 | 0 | 13 | 1 | 1900-01-03 02:00 | 0 | 0 | 0 | 1900-01-03 02:00 | 1900-01-24 22:00 | 1900-01-11 00:39 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 46.8 | 0 | 46.8 | 10.4268 | 55058.8235 | E
KANO INDUSTRIAL | TAMBURAWA | SHARADA | 33KV COCA COLA | URBAN | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0.085417 | 0 | 0 | 0 | 0.090278 | 1900-01-28 21:50 | 1900-01-26 01:10 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 19.2 | 0 | 19.2 | 0.67333 | 22588.2353 | A
KANO WEST | TAMBURAWA | PANSHEKARA | 33KV CHALAWA WATER WORKS | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-26 10:53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANO WEST | TAMBURAWA | MAIKALWA | 33KV TAMBURAWA WATER WORKS | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-22 20:53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO WEST | TAMBURAWA/TAM. W/PLANT | MAIKALWA | 33KV DR JAMIL GWAMNA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 05:34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV HADEJIA | URBAN | 4 | 0 | 4 | 0 | 0 | 0 | 3 | 1 | 1899-12-31 11:03 | 0 | 0 | 0 | 1899-12-31 11:03 | 1900-01-27 12:57 | 1900-01-24 05:24 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5 | 0 | 13.5 | 4.9326 | 15882.3529 | A
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV BIRNIWA | RURAL | 8 | 0 | 8 | 0 | 0 | 0 | 6 | 2 | -55.5368 | 0 | 0 | 0 | -55.5368 | 1900-03-25 12:53 | 1900-01-15 20:00 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5.2 | 0 | 5.2 | -39.0806 | 6117.6471 | D
JIGAWA NORTH | HADEJIA | GUMEL | 33KV GUMEL | RURAL | 4 | 0 | 4 | 0 | 0 | 0 | 2 | 2 | -57.3604 | 0 | 0 | 0 | -57.3604 | 1900-03-27 08:39 | 1900-01-09 00:23 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 3.6 | -51.6379 | 4235.2941 | D
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV KAFIN HAUSA | RURAL | 4 | 1 | 3 | 0 | 0 | 1 | 3 | 0 | -0.27708 | 0 | 0 | 0 | -0.27708 | 1900-01-29 06:39 | 1900-01-25 00:32 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 8.5 | 0.45563 | 10000 | A
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV YANLEMAN | RURAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-24 18:39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV UNIVERSITY | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
JIGAWA NORTH | GAGARAWA | GUMEL | 33KV RICE MILLS | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-28 14:56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
JIGAWA NORTH | GAGARAWA | GUMEL | 33KV GAGARAWA | URBAN | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0.34722 | 0 | 0 | 0 | 0.34722 | 1900-01-28 15:40 | 1900-01-28 13:33 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3.7 | 0 | 3.7 | 0.6325 | 4352.9412 | B
JIGAWA NORTH | GAGARAWA | GUMEL | 33KV GUJUNGU | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.48681 | 1900-01-28 12:19 | 1900-01-28 14:56 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0.097361 | 235.2941
JIGAWA SOUTH | DUTSE | BIRNIN KUDU | 33KV BIRNIN KUDU | RURAL | 14 | 1 | 10 | 1 | 0 | 0 | 12 | 2 | 1900-01-01 09:17 | 0 | 0 | 0 | 1900-01-01 09:17 | 1900-01-26 14:43 | 1900-01-14 20:45 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 38.2 | 0 | 38.2 | 6.7097 | 44941.1765 | B
JIGAWA SOUTH | DUTSE | DUTSE | 33KV JAHUN | RURAL | 13 | 0 | 13 | 0 | 0 | 0 | 7 | 2 | -134277.4424 | 0 | 0 | 0 | -134277.4424 | 2267-09-19 10:37 | 1900-01-10 14:14 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 28.1 | 0 | 28.1 | -290848.8673 | 33058.8235 | D
JIGAWA SOUTH | DUTSE | DUTSE | 33KV DUTSE | URBAN | 4 | 1 | 3 | 0 | 0 | 0 | 2 | 2 | 0.75069 | 0 | 0 | 0 | 0.75069 | 1900-01-28 05:59 | 1900-01-25 20:16 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 17.9 | 0 | 17.9 | 3.2023 | 21058.8235 | A
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV AJIWA WATER WORKS | URBAN | 7 | 0 | 4 | 2 | 0 | 0 | 3 | 3 | -42584.7375 | 0 | 0 | 0 | -42584.7194 | 2016-09-01 17:16 | 1900-01-25 11:06 | 6 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 19.1 | 0 | 19.1 | -21510.7102 | 22470.5882 | A
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV POWER HOUSE | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-28 16:01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV POLYTECHNIC | RURAL | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 20:02 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 3.5 | 0 | 4117.6471 | D
KATSINA NORTH | KATSINA | KATSINA CITY | 33KV KAITA | RURAL | 5 | 0 | 4 | 1 | 0 | 0 | 4 | 1 | 0.23264 | 0 | 0 | 0 | 0.23264 | 1900-01-28 18:25 | 1900-01-23 11:27 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22.4 | 0 | 22.4 | 1.017 | 26352.9412 | D
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV DANA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA NORTH | KATSINA | KATSINA CITY | 33KV KOFAR GUGA | URBAN | 3 | 0 | 3 | 0 | 0 | 0 | 2 | 1 | 0.45486 | 0 | 0 | 0 | 0.45486 | 1900-01-28 13:05 | 1900-01-22 19:53 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12.6 | 0 | 12.6 | 1.8589 | 14823.5294 | A
KATSINA NORTH | DAURA | DAURA | 33KV DAURA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-28 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA NORTH | DAURA | DAURA | 33KV MASHI | RURAL | 8 | 2 | 6 | 0 | 0 | 0 | 7 | 1 | 1900-01-01 13:43 | 0 | 0 | 0 | 1900-01-01 13:43 | 1900-01-26 10:17 | 1900-01-14 14:00 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 13.9 | 0 | 13.9 | 4.8381 | 16352.9412 | C
KATSINA NORTH | DAURA | DAURA | 33KV MAI ADUA | RURAL | 7 | 1 | 6 | 0 | 0 | 0 | 6 | 0 | -44779.3604 | 0 | 0 | 0 | -44779.3604 | 2022-09-05 08:39 | 1900-01-17 16:00 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 13 | 0 | 13 | -107471.3728 | 15294.1176 | E
KATSINA CENTRAL | DAURA | KANKIA | 33KV KAZAURE | RURAL | 3 | 1 | 2 | 0 | 0 | 1 | 1 | 1 | 0.58889 | 0 | 0 | 0 | 0.58889 | 1900-01-28 09:52 | 1900-01-19 01:01 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 4.2 | 0 | 4.2 | 0.93347 | 4941.1765 | C
KATSINA CENTRAL | KANKIA | KANKIA | 33KV DANBATTA | RURAL | 2 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | -44775.9993 | 0 | 0 | 0 | -44775.9993 | 2022-09-01 23:59 | 1900-01-08 20:06 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3.1 | 0 | 3.1 | -94029.623 | 3647.0588 | E
KATSINA CENTRAL | KANKIA | KANKIA | 33KV AMPRI GLOBAL | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-27 08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA CENTRAL | KANKIA | KANKIA | 33KV MUSAWA | RURAL | 9 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | -179104.6861 | 0 | 0 | 0 | -179104.6861 | 2390-06-13 16:28 | 1900-01-14 08:00 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 29.5 | 0 | 29.5 | -653737.8186 | 34705.8824 | D
KATSINA CENTRAL | KANKIA | DUTSENMA | 33KV DUTSENMA | RURAL | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -44775.9688 | 0 | 0 | 0 | -44775.9688 | 2022-09-01 23:15 | 1900-01-24 05:00 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 2.3 | -102984.7281 | 2705.8824 | C
KATSINA CENTRAL | KANKIA | DUTSENMA | 33KV WATARI | RURAL | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | -44779.7153 | 0 | 0 | 0 | -44779.7153 | 2022-09-05 17:10 | 1900-01-23 21:00 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | -4477.869 | 588.2353
KATSINA SOUTH | FUNTUA | MALUMFASHI | 33KV MALUMFASHI | RURAL | 2 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | -44778.6653 | 0 | 0 | 0 | -44778.6653 | 2022-09-04 15:58 | 1900-01-09 16:10 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 3.9 | -80601.4898 | 4588.2353 | D
KATSINA SOUTH | FUNTUA | MALUMFASHI | 33KV MAMMAN NASIR | URBAN | 11 | 0 | 10 | 1 | 0 | 1 | 6 | 1 | -134395.1146 | 0 | 0 | 0 | -134395.1146 | 2268-01-15 02:45 | 1900-01-11 22:54 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 14.5618 | 0 | 14.5618 | -246352.7531 | 17131.5359 | B
KATSINA SOUTH | FUNTUA | FUNTUA | 33KV DANDUME | RURAL | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0.37778 | 0 | 0 | 0 | 0.37778 | 1900-01-28 14:56 | 1900-01-10 16:07 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5.3 | 0 | 5.3 | 0.8025 | 6235.2941 | E
KATSINA SOUTH | FUNTUA | FUNTUA | 33KV KATSINA ROAD | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-25 07:51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA SOUTH | FUNTUA | FUNTUA | 33KV TEXTILE | URBAN | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | -44783.9924 | 0 | 0 | 0 | -44783.9924 | 2022-09-09 23:49 | 1900-01-24 09:25 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 9.9 | 0 | 9.9 | -277661.857 | 11647.0588 | A
KANO NORTH | 15MVA TR1 DAN AGUNDI | KANO CITY | 11KV KOFAR NASSARAWA | URBAN | 5 | 2 | 2 | 1 | 0 | 2 | 1 | 2 | 0.7375 | 0 | 0 | 0 | 0.7375 | 1900-01-28 06:18 | 1900-01-15 02:22 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 14.4 | 0 | 14.4 | 2.5874 | 16941.1765 | C
KANO INDUSTRIAL | 15MVA TR1 DAN AGUNDI | ZOO ROAD | 11KV AJASA | URBAN | 5 | 2 | 1 | 0 | 0 | 1 | 1 | 2 | 0.53056 | 0.13194 | 0 | 0 | 0.75347 | 1900-01-28 05:55 | 1900-01-16 12:38 | 2 | 4 | 0 | 0 | 1 | 2 | 0 | 1 | 3 | 1 | 9.6 | 0 | 9.6 | 1.5207 | 11294.1176 | A
KANO NORTH | 15MVA TR1 DAN AGUNDI | KANO CITY | 11KV IBRAHIM TAIWO | URBAN | 3 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 0.94444 | 0 | 0 | 0 | 0.94444 | 1900-01-28 01:20 | 1900-01-16 09:18 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3.3 | 0 | 3.3 | 0.33104 | 3882.3529 | C
KANO NORTH | 15MVA TR2 DAN AGUNDI | KANO CITY | 11KV CITY | URBAN | 2 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0.18889 | 0 | 0 | 0 | 0.18889 | 1900-01-28 19:28 | 1900-01-15 15:05 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3.3 | 0 | 3.3 | 0.28562 | 3882.3529 | C
KANO NORTH | 15MVA TR2 DAN AGUNDI | KANO CITY | 11KV KOFAR NAISA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-12 04:35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO NORTH | 15MVA TR1 GORON DUTSE | KANO CITY | 11KV JAKARA | URBAN | 3 | 0 | 2 | 1 | 0 | 0 | 1 | 2 | 0.65764 | 0 | 0 | 0 | 0.65764 | 1900-01-28 08:13 | 1900-01-04 15:34 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4.4 | 0 | 4.4 | 0.99194 | 5176.4706 | D
KANO NORTH | 15MVA TR1 GORON DUTSE | RIJIYAR ZAKI | 11KV AMINU KANO | URBAN | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1899-12-31 23:55 | 0.099306 | 0 | 0 | 1900-01-01 02:18 | 1900-01-26 21:42 | 1900-01-06 05:27 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 3.4 | 0 | 3.4 | 6.7882 | 4000 | C
KANO NORTH | 15MVA TR2 GORON DUTSE | RIJIYAR ZAKI | 11KV SANI MAINAGGE | URBAN | 3 | 1 | 1 | 1 | 0 | 0 | 1 | 2 | 1899-12-31 05:59 | 0 | 0 | 0 | 1899-12-31 05:59 | 1900-01-27 18:01 | 1900-01-05 23:36 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6.3 | 0 | 6.3 | 2.3708 | 7411.7647 | C
KANO NORTH | 15MVA TR2 GORON DUTSE | RIJIYAR ZAKI | 11KV KABUGA | URBAN | 6 | 0 | 0 | 3 | 0 | 0 | 2 | 3 | -44779.7285 | 0 | 0 | 0 | -44778.6632 | 2022-09-04 15:55 | 1900-01-06 00:41 | 4 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 21.4 | 0 | 21.4 | -156723.9619 | 25176.4706 | B
KANO NORTH | 7.5MVA TR1 NIPP RADIO HOUSE | KANO CITY | 11KV BELLO DANDAGO | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.17917 | 0 | 0 | 0 | 0.17917 | 1900-01-28 19:42 | 1900-01-14 01:21 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0.03 | 0.005375 | 35.2941 | A
KANO NORTH | 15MVA TR1 ADO BAYERO | KANO CITY | 11KV SAGAGI | URBAN | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 1899-12-31 01:30 | 0 | 0 | 0 | 1899-12-31 01:30 | 1900-01-27 22:30 | 1900-01-11 13:34 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 2.9 | 1.6748 | 3411.7647 | D
KANO NORTH | 15MVA TR1 BUKAVU | RIJIYAR ZAKI | 11KV BACHIRAWA | URBAN | 4 | 1 | 2 | 1 | 0 | 0 | 0 | 3 | -44782.8639 | 0 | 0 | 0 | -44782.8639 | 2022-09-08 20:44 | 1900-01-05 01:24 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 2.5 | 1.474 | 2941.1765 | C
KANO CENTRAL | 15MVA TR1 BUKAVU | SABON GARI | 11KV NOMANSLAND | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-07 22:59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO NORTH | 15MVA TR2 BUKAVU | IDH | 11KV FEDERAL SECRETARIAT | URBAN | 4 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 0.57292 | 0 | 0 | 0 | 0.625 | 1900-01-28 09:00 | 1900-01-05 15:23 | 3 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 5.5 | 0 | 5.5 | 1.1875 | 6470.5882 | C
KANO NORTH | 15MVA TR2 BUKAVU | IDH | 11KV ORTHOPAEDIC | URBAN | 4 | 2 | 2 | 0 | 0 | 1 | 0 | 3 | 0.96875 | 0 | 0 | 0 | 0.96875 | 1900-01-28 00:45 | 1900-01-06 08:44 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4.3 | 0 | 4.3 | 1.414 | 5058.8235 | C
KANO CENTRAL | 15MVA TR2 BUKAVU | SABON GARI | 11KV FANISAU | URBAN | 4 | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 1900-01-02 21:34 | 0 | 0 | 0 | 1900-01-02 21:34 | 1900-01-25 02:26 | 1900-01-05 00:42 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 5.3 | 3.1242 | 6235.2941 | D
KANO NORTH | 15MVA TR1 I.D.H. | IDH | 11KV FAGGE | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0.072917 | 0 | 0 | 0 | 0.072917 | 1900-01-28 22:15 | 1900-01-11 16:24 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.9 | 0 | 1.9 | 0.13854 | 2235.2941 | C
KANO NORTH | 15MVA TR2 I.D.H. | IDH | 11KV GWAMMAJA | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.056944 | 1900-01-28 22:38 | 1900-01-08 00:32 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2.2 | 0 | 2.2 | 0.12528 | 2588.2353 | D
KANO CENTRAL | 15MVA TR2 I.D.H. | SABON GARI | 11KV SABON GARI | URBAN | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0.28611 | 0 | 0 | 0 | 0.29861 | 1900-01-28 16:50 | 1900-01-12 17:00 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4 | 0 | 4 | 0.46042 | 4705.8824 | B
KANO CENTRAL | 15MVA TR3 I.D.H. | SABON GARI | 11KV ABUJA ROAD | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-12 17:08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO NORTH | 15MVA TR3 I.D.H. | IDH | 11KV KOKI | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | -0.86458 | 0 | 0 | 0 | -0.86458 | 1900-01-29 20:45 | 1900-01-11 07:03 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KANO CENTRAL | 15MVA TR1 SMALL SCALE | BOMPAI | 11KV TUDUN MURTALA | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | -44784.2417 | 0 | 0 | 0 | -44784.2417 | 2022-09-10 05:48 | 1900-01-11 16:15 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 1.2 | -53741.09 | 1411.7647 | D
KANO CENTRAL | 15MVA TR1 SMALL SCALE | BOMPAI | 11KV RIMIN KEBE | URBAN | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0.091667 | 0 | 0 | 0 | 0.091667 | 1900-01-28 21:48 | 1900-01-12 00:34 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.6 | 0 | 2.6 | 0.23833 | 3058.8235 | D
KANO INDUSTRIAL | 15MVA TR1 SHARADA | SHARADA | 11KV HOUSING ESTATE | URBAN | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.18264 | -44784.4028 | 0 | 0 | -44784.2201 | 2022-09-10 05:17 | 1900-01-15 21:03 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 9.1 | 0 | 9.1 | -161223.4607 | 10705.8824 | B
KANO INDUSTRIAL | 15MVA TR1 SHARADA | SHARADA | 11KV NNDC | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-12 21:51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO INDUSTRIAL | 15MVA TR2 SHARADA | ZOO ROAD | 11KV TUKUNTAWA | URBAN | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.20903 | 0 | 0 | 0 | 0.20903 | 1900-01-28 18:59 | 1900-01-10 09:01 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0.41806 | 2352.9412 | C
KANO INDUSTRIAL | 15MVA TR2 SHARADA | ZOO ROAD | 11KV SHARADA INDUSTRIAL | URBAN | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0.625 | 0 | 0 | 0 | 0.625 | 1900-01-28 09:00 | 1900-01-13 09:11 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 4.9 | 1.5717 | 5764.7059 | A
KANO INDUSTRIAL | 15MVA TR1 GONGONI | DORAYI | 11KV JAEN | URBAN | 5 | 5 | 0 | 0 | 0 | 0 | 4 | 1 | 1899-12-31 00:14 | 0 | 0 | 0 | 1899-12-31 00:14 | 1900-01-27 23:46 | 1900-01-09 15:32 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12.7 | 0 | 12.7 | 2.1057 | 14941.1765 | D
KANO INDUSTRIAL | 15MVA TR1 GONGONI | DORAYI | 11KV CHIRANCI | URBAN | 3 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | -44781.1562 | 0 | 0 | 0 | -44781.1063 | 2022-09-07 02:33 | 1900-01-10 20:55 | 2 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 14.5 | 0 | 14.5 | -134343.2031 | 17058.8235 | D
KANO INDUSTRIAL | 15MVA TR1 GONGONI | SHARADA | 11KV MUNDADU | URBAN | 2 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0.68889 | 0 | 0 | 0 | 0.68889 | 1900-01-28 07:28 | 1900-01-14 20:23 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.30833 | 1176.4706 | D
KANO INDUSTRIAL | 7.5MVA TR2 GONGONI | SHARADA | 11KV DALA FOODS | URBAN | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.29167 | 0.076389 | 0 | 0 | 0.36806 | 1900-01-28 15:10 | 1900-01-24 05:36 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 2 | 0.58333 | 2352.9412 | A
KANO INDUSTRIAL | 15MVA TR1 ZARIA ROAD | AKTH | 11KV KARKASARA | URBAN | 7 | 1 | 1 | 4 | 0 | 0 | 2 | 4 | #VALUE! | 0.17917 | 0 | 0 | #VALUE! | #VALUE! | 1900-01-12 15:40 | 6 | 6 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 27.1 | 0 | 27.1 | #VALUE! | 31882.3529 | C
KANO EAST | 15MVA TR1 ZARIA ROAD | HOTORO | 11KV KUNDILA | URBAN | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0.73542 | 0 | 0 | 0 | 0.73542 | 1900-01-28 06:21 | 1900-01-10 21:29 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 2.3 | 0.53187 | 2705.8824 | C
KANO INDUSTRIAL | 15MVA TR3 ZARIA ROAD | AKTH | 11KV SALLARI | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0.097222 | 0 | 0 | 0 | 0.097222 | 1900-01-28 21:40 | 1900-01-11 18:42 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO EAST | 15MVA TR2 ZARIA ROAD | HOTORO | 11KV UNGUWA UKU | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-10 13:23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO EAST | 15MVA TR2 ZARIA ROAD | HOTORO | 11KV HOTORO | URBAN | 6 | 0 | 2 | 2 | 0 | 0 | 1 | 5 | 0.90139 | 0 | 0 | 0 | 1899-12-31 02:38 | 1900-01-27 21:22 | 1900-01-11 16:30 | 4 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 4 | 0 | 7.9 | 0 | 7.9 | 1.232 | 9294.1176 | C
KANO INDUSTRIAL | 15MVA TR3 ZARIA ROAD | AKTH | 11KV HAUSAWA | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.097222 | 0 | 0 | 0 | 0.097222 | 1900-01-28 21:40 | 1900-01-14 03:31 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.3 | 0 | 1.3 | 0.12639 | 1529.4118 | C
KANO INDUSTRIAL | 15MVA TR3 ZARIA ROAD | AKTH | 11KV MARHABA | URBAN | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.021528 | 0 | 0 | 0 | 0.021528 | 1900-01-28 23:29 | 1900-01-13 02:44 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.5 | 0 | 2.5 | 0.053819 | 2941.1765 | C
KANO INDUSTRIAL | 15MVA TR1 ABATTOIR | DORAYI | 11KV CERAMIC | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-26 17:09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO INDUSTRIAL | 15MVA TR1 ABATTOIR | DORAYI | 11KV NBC | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-26 07:12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO WEST | 15MVA TR1 ABATTOIR | PANSHEKARA | 11KV ZAWACIKI | URBAN | 2 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0.15694 | 0 | 0 | 0 | 0.15694 | 1900-01-28 20:14 | 1900-01-16 03:35 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3.8 | 0 | 3.8 | 0.052778 | 4470.5882 | C
KANO WEST | 7.5MVA TR1 CHALLAWA | PANSHEKARA | 11KV CHALAWA WATER PLANT | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-26 10:01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANO WEST | 7.5MVA TR2 CHALLAWA | PANSHEKARA | 11KV PANSHEKARA | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1125 | 1900-01-28 21:18 | 1900-01-22 07:15 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO WEST | 15MVA TR1 TAMBURAWA | MAIKALWA | 11KV TAMBURAWA WATER PLANT | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-22 00:29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO WEST | 7.5MVA TR1 NA'IBAWA | MAIKALWA | 11KV YANLEMO | URBAN | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0.67153 | 0 | 0 | 0 | 0.83194 | 1900-01-28 04:02 | 1900-01-14 12:21 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 4.1 | 0 | 4.1 | 1.6288 | 4823.5294 | C
KANO WEST | 7.5MVA TR1 NA'IBAWA | MAIKALWA | 11KV MASARAUTA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-15 22:53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO WEST | 7.5MVA TR1 NIPP LAW SCHOOL | KWANAR DANGORA | 11KV CAMPUS | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-05 23:13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO WEST | 7.5MVA TR1 NIPP LAW SCHOOL | KWANAR DANGORA | 11KV TIGA | RURAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-04 12:06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
KANO CENTRAL | 15MVA TR1 CLUB | KEDCO HQ | 11KV AHMADU BELLO | URBAN | 10 | 4 | 4 | 1 | 0 | 3 | 3 | 3 | 0.95278 | 0.29792 | 0 | 0 | 1899-12-31 06:01 | 1900-01-27 17:59 | 1900-01-20 00:52 | 9 | 9 | 0 | 0 | 1 | 0 | 0 | 1 | 7 | 1 | 24.1 | 0 | 24.1 | 2.702 | 28352.9412 | A
KANO CENTRAL | 15MVA TR1 CLUB | BADAWA | 11KV RACE COURSE | URBAN | 2 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | -44783.7569 | 0 | 0 | 0 | -44783.7569 | 2022-09-09 18:10 | 1900-01-18 08:31 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 2.9 | -62697.2175 | 3411.7647 | B
KANO CENTRAL | 15MVA TR1 CLUB | BADAWA | 11KV BADAWA | URBAN | 4 | 3 | 0 | 0 | 0 | 1 | 2 | 1 | 0.77083 | 0 | 0 | 0 | 0.77083 | 1900-01-28 05:30 | 1900-01-20 06:39 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12.2 | 0 | 12.2 | 2.3147 | 14352.9412 | B
KANO CENTRAL | 15MVA TR2 CLUB | KEDCO HQ | 11KV BANK ROAD | URBAN | 8 | 6 | 2 | 0 | 0 | 2 | 5 | 1 | 1900-02-28 17:34 | 0 | 0 | 0 | 1900-02-28 17:34 | -30.7319 | 1900-01-19 07:52 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 18 | 0 | 18 | 181.5049 | 21176.4706 | A
KANO CENTRAL | 15MVA TR2 CLUB | KEDCO HQ | 11KV AUDU BAKO | URBAN | 2 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0.24722 | 0 | 0 | 0 | 0.24722 | 1900-01-28 18:04 | 1900-01-22 05:20 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3.8 | 0 | 3.8 | 0.39972 | 4470.5882 | A
KANO CENTRAL | 15MVA TR3 CLUB | SABON GARI | 11KV MURTALA MUHAMMED | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-13 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO CENTRAL | 15MVA TR3 CLUB | BADAWA | 11KV LAMIDO | URBAN | 3 | 1 | 2 | 0 | 0 | 0 | 2 | 1 | 0.67153 | 0 | 0 | 0 | 0.67153 | 1900-01-28 07:53 | 1900-01-12 06:44 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 0 | 4 | 1.1639 | 4705.8824 | C
KANO CENTRAL | 15MVA TR1 FARM CENTER | KEDCO HQ | 11KV DR BALA | URBAN | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0.41597 | 0.18125 | 0 | 0 | 0.59722 | 1900-01-28 09:40 | 1900-01-22 11:33 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0.7 | 0 | 0.7 | 0.12688 | 823.5294 | A
KANO EAST | 15MVA TR2 FARM CENTER | HOTORO | 11KV TARAUNI | URBAN | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 0.38403 | 0 | 0 | 0 | -44784.0611 | 2022-09-10 01:28 | 1900-01-17 21:58 | 2 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 6.7 | 0 | 6.7 | -89567.979 | 7882.3529 | A
KANO EAST | 7.5MVA TR2 MARIRI | HOTORO | 11KV DANLADI NASIDI | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.22917 | 1900-01-28 18:30 | 1900-01-13 13:27 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO EAST | 7.5MVA TR2 MARIRI | HOTORO | 11KV MAIDUGURI ROAD | URBAN | 6 | 1 | 1 | 2 | 1 | 0 | 3 | 2 | 1900-01-01 15:35 | 0 | 0 | 0 | 1900-01-01 17:15 | 1900-01-26 06:45 | 1900-01-07 23:06 | 5 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 4.9 | 0 | 4.9 | 0.36278 | 5764.7059 | C
KANO EAST | 7.5MVA TR1 MARIRI | HOTORO | 11KV FARAWA | URBAN | 3 | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 1900-02-27 07:10 | 0 | 0 | 0 | 1900-02-27 07:45 | -29.3229 | 1900-01-08 12:33 | 2 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 4 | 0 | 4 | 0.097222 | 4705.8824 | C
KANO EAST | 15MVA TR1 JOGANA | KAWAJI | 11KV TALAMIZ | URBAN | 7 | 1 | 4 | 1 | 0 | 0 | 3 | 3 | 1900-01-02 06:03 | 0.25764 | 0 | 0 | 1900-01-02 12:14 | 1900-01-25 11:46 | 1900-01-11 10:45 | 6 | 6 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 7.01 | 0 | 7.01 | 4.9441 | 8247.0588 | D
KANO EAST | 15MVA TR1 JOGANA | KAWAJI | 11KV TOKARAWA | URBAN | 4 | 0 | 0 | 0 | 3 | 0 | 1 | 3 | 0.66181 | 0 | 0 | 0 | 0.66181 | 1900-01-28 08:07 | 1900-01-15 17:48 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 3 | 0.24222 | 3529.4118 | A
KANO EAST | 15MVA TR1 JOGANA | KAWAJI | 11KV TSAMIYA BABBA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-13 17:02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KANO EAST | 7.5MVA TR1 WUDIL | WUDIL | 11KV MAKAMA | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.36736 | 0 | 0 | 0 | 0.36736 | 1900-01-28 15:11 | 1900-01-19 22:12 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 1.1 | 0.4041 | 1294.1176 | C
| 7.5MVA TR1 WUDIL |  | 11KV KUT | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
|  |  | 11KV WUDIL COMMERCIAL | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-11 18:28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANO EAST | 15MVA TR1 KAWAJI | KAWAJI | 11KV DAKATA | URBAN | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.032639 | 0 | 0 | 0 | 0.032639 | 1900-01-28 23:13 | 1900-01-16 18:38 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO EAST | 15MVA TR1 KAWAJI | KAWAJI | 11KV YANKABA | URBAN | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.20347 | 0.14514 | 0 | 0 | 0.34861 | 1900-01-28 15:38 | 1900-01-17 06:43 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KANO CENTRAL | 15MVA TR1 BRISCOE | BOMPAI | 11KV MAIMALARI | URBAN | 3 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 0.52847 | 0 | 0 | 0 | 0.52847 | 1900-01-28 11:19 | 1900-01-20 11:06 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1.5 | 0 | 1.5 | 0.54062 | 1764.7059 | A
KANO CENTRAL | 15MVA TR1 BRISCOE | SABON GARI | 11KV TUDUN WADA | URBAN | 3 | 3 | 0 | 0 | 0 | 1 | 0 | 2 | 1899-12-31 03:06 | 0 | 0 | 0 | 1899-12-31 03:06 | 1900-01-27 20:54 | 1900-01-13 21:38 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | D
KANO CENTRAL | 15MVA TR1 BRISCOE | BADAWA | 11KV YUSUF ROAD | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.78958 | 0 | 0 | 0 | 0.78958 | 1900-01-28 05:03 | 1900-01-20 14:31 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0.4 | 0.31583 | 470.5882 | A
KANO CENTRAL | 15MVA TR2 BRISCOE | BOMPAI | 11KV INDEPENDENCE | URBAN | 7 | 4 | 2 | 0 | 0 | 1 | 1 | 3 | 0.54097 | 0.17153 | 0 | 0 | 0.7125 | 1900-01-28 06:54 | 1900-01-17 15:18 | 6 | 6 | 0 | 0 | 1 | 0 | 0 | 0 | 6 | 0 | 4.4 | 0 | 4.4 | 0.36833 | 5176.4706 | B
KANO CENTRAL | 15MVA TR2 BRISCOE | SABON GARI | 11KV GWAGWARWA | URBAN | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.81597 | 0 | 0 | 0 | 0.81597 | 1900-01-28 04:25 | 1900-01-14 01:16 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 1.6319 | 2352.9412 | D
KANO CENTRAL | 15MVA TR3 BRISCOE | BOMPAI | 11KV BOMPAI | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 00:52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KANO CENTRAL | 7.5MVA TR1 NIPP PRP | SABON GARI | 11KV KAURA GOJE | URBAN | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.46528 | 0 | 0 | 0 | 0.46528 | 1900-01-28 12:50 | 1900-01-10 16:26 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.46528 | 1176.4706 | D
KANO CENTRAL | 7.5MVA TR1 NIPP PRP | SABON GARI | 11KV AIRPORT ROAD | URBAN | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0.48403 | 0 | 0 | 0 | 0.48403 | 1900-01-28 12:23 | 1900-01-14 18:53 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.5 | 0 | 2.5 | 0.58167 | 2941.1765 | A
KATSINA CENTRAL | 7.5MVA TR1 BICHI | KANKIA | 11KV BICHI TOWN | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-02 13:28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KANO NORTH | 15MVA TR2 BUK | RIJIYAR ZAKI | 11KV GWARZO ROAD | URBAN | 5 | 0 | 1 | 4 | 0 | 0 | 1 | 4 | 1899-12-31 15:25 | 0 | 0 | 0 | 1899-12-31 15:25 | 1900-01-27 08:35 | 1900-01-10 07:16 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.7 | 0 | 0.7 | 0.26153 | 823.5294 | A
KANO NORTH | 15MVA TR1 BUK | RIJIYAR ZAKI | 11KV NEW SITE | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-09 18:03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
JIGAWA NORTH | 7.5MVA TR1 HADEJIA | HADEJIA | 11KV MAJE | URBAN | 7 | 3 | 1 | 3 | 0 | 0 | 4 | 3 | 1900-01-01 02:26 | 0 | 0 | 0 | 1900-01-01 02:53 | 1900-01-26 21:07 | 1900-01-17 09:46 | 6 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 18.9 | 0 | 18.9 | 6.098 | 22235.2941 | C
JIGAWA NORTH | 7.5MVA TR2 HADEJIA | HADEJIA | 11KV SHAGARI | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-17 19:47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
JIGAWA NORTH | 7.5MVA TR2 NIPP HADEJIA | HADEJIA | 11KV JAMAARE | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-20 16:31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
JIGAWA NORTH | 7.5MVA TR1 NIPP HADEJIA | HADEJIA | 11KV FANTAI | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-23 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
JIGAWA NORTH | 7.5MVA TR1 NIPP MALAMADORI | GUMEL | 11KV MAKWALLA | URBAN | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0.10486 | 0 | 0 | 0 | 0.28819 | 1900-01-28 17:05 | 1900-01-07 18:03 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1.2 | 0 | 1.2 | 0.17292 | 1411.7647 | D
JIGAWA NORTH | 7.5MVA TR1 NIPP GUMEL | GUMEL | 11KV LAUTAI | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 02:26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
JIGAWA SOUTH | 7.5MVA TR1 DUTSE | DUTSE | 11KV GOVERNMENT HOUSE DUTSE | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 13:19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
JIGAWA SOUTH | 7.5MVA TR1 DUTSE | DUTSE | 11KV LIMAWA | URBAN | 3 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0.42639 | 0 | 0 | 0 | 0.45903 | 1900-01-28 12:59 | 1900-01-21 15:30 | 2 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1.5 | 0 | 1.5 | 0.31562 | 1764.7059 | C
JIGAWA SOUTH | 7.5MVA TR1 DUTSE | DUTSE | 11KV GARU | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-23 08:04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
JIGAWA SOUTH | 7.5MVA TR1 DUTSE NIPP | DUTSE | 11KV SANI ABACHA WAY | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0.29097 | 0 | 0 | 0 | 0.29097 | 1900-01-28 17:01 | 1900-01-23 05:12 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0.8 | 0.23278 | 941.1765 | B
JIGAWA SOUTH | 7.5MVA TR2 DUTSE NIPP | DUTSE | 11KV TAKUR | URBAN | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0.31111 | 0 | 0 | 0 | 0.31111 | 1900-01-28 16:32 | 1900-01-22 07:37 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
JIGAWA SOUTH | 7.5MVA TR1 BIRNIN KUDU | BIRNIN KUDU | 11KV SCHOOL OF NURSING | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-04 16:24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
JIGAWA SOUTH | 7.5MVA TR1 BIRNIN KUDU | BIRNIN KUDU | 11KV MAJESTIC | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-04 16:24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KATSINA NORTH | 15MVA TR1 IBB WAY KATSINA | KATSINA URBAN | 11KV GRA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-17 16:23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KATSINA NORTH | 15MVA TR3 IBB WAY KATSINA | KATSINA URBAN | 11KV LOW COST | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.10208 | 0 | 0 | 0 | 0.10208 | 1900-01-28 21:33 | 1900-01-22 21:38 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.4 | 0 | 1.4 | 0.14292 | 1647.0588 | B
KATSINA NORTH | 7.5MVA TR2 IBB WAY KATSINA | KATSINA CITY | 11KV KANO ROAD | URBAN | 3 | 0 | 3 | 0 | 0 | 0 | 1 | 2 | 0.43819 | 0 | 0 | 0 | 0.43819 | 1900-01-28 13:29 | 1900-01-17 01:34 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 9.3 | 0 | 9.3 | 1.2503 | 10941.1765 | C
KATSINA NORTH | 15MVA TR1 IBB WAY KATSINA | KATSINA CITY | 11KV ARMY BARRACKS | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0.34167 | 0 | 0 | 0 | 0.34167 | 1900-01-28 15:48 | 1900-01-12 06:42 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 1.025 | 3529.4118 | D
KATSINA NORTH | 15MVA TR3 IBB WAY KATSINA | KATSINA URBAN | 11KV KOFAR MARUSA | URBAN | 2 | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 0.72986 | 0 | 0 | 0 | 0.72986 | 1900-01-28 06:29 | 1900-01-11 09:54 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 4.3 | 1.7766 | 5058.8235 | D
KATSINA NORTH | 15MVA TR3 IBB WAY KATSINA | KATSINA URBAN | 11KV DANDAGORO | URBAN | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0.3875 | 0 | 0 | 0 | 0.3875 | 1900-01-28 14:42 | 1900-01-16 16:48 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4.8 | 0 | 4.8 | 0.93 | 5647.0588 | C
KATSINA NORTH | 7.5MVA TR1 KOFAR GUGA KATSINA | KATSINA CITY | 11KV HOSPITAL ROAD | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-15 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KATSINA NORTH | 7.5MVA TR2 KOFAR GUGA KATSINA | KATSINA CITY | 11KV FMC | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-15 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KATSINA NORTH | 7.5MVA TR2 KOFAR GUGA KATSINA | KATSINA CITY | 11KV DUTSEN SAFE | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-15 16:05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KATSINA NORTH | 7.5MVA TR1 KOFAR GUGA KATSINA | KATSINA CITY | 11KV NATSINTA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 18:23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA NORTH | 7.5MVA TR1 FADAMA NIPP | KATSINA URBAN | 11KV HASSAN USMAN ROAD | URBAN | 4 | 0 | 4 | 0 | 0 | 0 | 1 | 2 | 0.87708 | 0 | 0 | 0 | 0.87708 | 1900-01-28 02:57 | 1900-01-20 16:03 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 16.6 | 0 | 16.6 | 4.4592 | 19529.4118 | B
KATSINA NORTH | 7.5MVA TR1 FADAMA NIPP | KATSINA CITY | 11KV APEX | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-25 08:22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA NORTH | 7.5MVA TR2 FADAMA NIPP | KATSINA URBAN | 11KV NAGOGGO | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-11 10:41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KATSINA NORTH | 7.5MVA TR2 FADAMA NIPP | KATSINA URBAN | 11KV KADARKO | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-20 16:03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KATSINA NORTH | 7.5MVA TR1 KOFAR SAURI NIPP | KATSINA CITY | 11KV MUHAMMED DIKKO | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-16 12:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KATSINA CENTRAL | 7MVA TR1 NIPP MUSAWA | KANKIA | 11KV KOFAR FADA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-06 14:09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KATSINA CENTRAL | 7MVA TR1 NIPP MUSAWA | KANKIA | 11KV MATAZU | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-06 09:19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
KATSINA CENTRAL | 7.5MVA TR1 KAZAURE | KANKIA | 11KV KANTI | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -44784.2569 | 0 | 0 | 0 | -44784.2569 | 2022-09-10 06:10 | 1900-01-17 04:41 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 1.2 | -53741.1083 | 1411.7647 | C
KATSINA CENTRAL | 7.5MVA TR1 KAZAURE | KANKIA | 11KV DANTUNKU | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-17 22:29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KATSINA NORTH | 7.5MVA TR1 DAURA NIPP | DAURA | 11KV DAURAMA | URBAN | 2 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0.54931 | 0 | 0 | 0 | 0.54931 | 1900-01-28 10:49 | 1900-01-23 01:08 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 0 | 4 | 1.0986 | 4705.8824 | B
KATSINA NORTH | 7.5MVA TR2 DAURA NIPP | DAURA | 11KV BAYAJIDDA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-22 11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV JABIRI | URBAN | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0.072222 | 0 | 0 | 0 | 0.072222 | 1900-01-28 22:16 | 1900-01-19 08:04 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.7 | 0 | 2.7 | 0.195 | 3176.4706 | C
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV DUTSEN REME | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-21 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV INDUSTRIAL | URBAN | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -44776.8125 | 0 | 0 | 0 | -44776.8125 | 2022-09-02 19:30 | 1900-01-24 04:47 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0.8 | -35821.45 | 941.1765 | A
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV TOWN | URBAN | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | -44776.4132 | 0 | 0 | 0 | -44776.4132 | 2022-09-02 09:55 | 1900-01-20 08:05 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 3.7 | -94030.5809 | 4352.9412 | C
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV NAKOWA | URBAN | 3 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | -89566.075 | 0 | 0 | 0 | -89566.075 | 2145-04-20 01:48 | 1900-01-18 19:11 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 9.4 | 0 | 9.4 | -277655.3027 | 11058.8235 | C
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV MAI RUWA | URBAN | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 1900-01-29 05:20 | 0 | 0 | 0 | 1900-01-29 05:20 | -0.22222 | 1900-01-19 23:10 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.2 | 0 | 1.2 | 18.1333 | 1411.7647 | E
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV FUNTUA TEXTILE MILL | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-23 15:45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV FUNTUA WATER WORKS | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-22 08:18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
KATSINA SOUTH | 7.5MVA TR1 MALUMFASHI | MALUMFASHI | 11KV BCGA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-10 08:49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
KATSINA SOUTH | 7.5MVA TR1 MALUMFASHI | MALUMFASHI | 11KV GALADIMA | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 | 1900-01-10 11:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
Total |  |  |  |  | 40 | 9 | 13 | 16 |  |  |  |  | -268754.0083 | 0.25417 | 0 | 0 | -268753.3125 |  |  | 38 | 39 | 0 | 0 | 1 | 1 | 0 | 1 | 24 | 1 |  |  |  |  | 354000
[14 empty] | TOTAL HOURS IN THE MONTH= |  | 1900-01-29
Remarks : Fault type are
[5 empty] | TL | Tripping due to Line fault
[5 empty] | TS | Tripping due to S/S fault
[5 empty] | PC | Planned shutdown for construction activity
[5 empty] | PM | Planned shutdown for O&M activity
[5 empty] | SE | Shutdown on Emergency
[5 empty] | UF | Tripped due to under-frequency
[5 empty] | O/C | Overcurrent Fault
[5 empty] | E/F | Earth Fault
[5 empty] | NO RI | No Relay Indication
[5 empty] | O/C & E/F | Overcurrent & Earth Fault
[5 empty] | YES | Field discovery during patrols
[5 empty] | NO | No Discovery upon Patrols
[5 empty] | Transient | Transient faults
Formulas:
Available Hours for Service = Q199-[Total Outage Duration]
Total Hours in Service = Table436[[#This Row],[Total Hours in Service]]
Outage Duration of Fault = SUBTOTAL(109,Table4[Outage Duration of Fault])
Duration of Planned Outage = SUBTOTAL(109,Table4[Duration of Planned Outage])
Duration of S/S Fault = SUBTOTAL(109,Table4[Duration of S/S Fault])
Total Outage Duration = SUBTOTAL(109,Table4[Total Outage Duration])

## Supply Hours
Region | Transmission/ Injection Station | TSP | Feeder | Band | Min Daily Hours | Min Hrs | Peak Load | Total Available Hours for Service | Connected Capacity per feeder (KVA) | Actual Min Hours Expected till date | Total Hours in Service | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
KANO INDUSTRIAL | KUMBOTSO | SHARADA | 33KV DANGOTE | A | 0.83333 | 20 | 19.4 | 2022-09-08 13:20 | 60100 | 1900-01-24 | 1900-01-25 22:00 | 0.66667 | 0.79167 | 0.79167 | 0.875 | 1899-12-31 | 0.91667 | 0.95833 | 0.95833 | 0.91667 | 1899-12-31 | 1899-12-31 | 0.875 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.91667 | 0.79167 | 0.41667 | 0.33333 | 1899-12-31 | 0.95833 | 0.58333 | 1899-12-31 | 0.66667 | 0.91667 | 0.75 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.91667
KANO INDUSTRIAL | KUMBOTSO | ZOO ROAD | 33KV ANGELS | A | 0.83333 | 20 | 18.3 | 1900-01-28 08:52 | 51000 | 1900-01-24 | 1900-01-27 19:00 | 0.91667 | 0.95833 | 1899-12-31 | 0.875 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.875 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.66667 | 0.83333 | 0.95833 | 0.58333 | 1899-12-31 | 1899-12-31 | 0.58333 | 1899-12-31 | 0.91667 | 0.95833 | 1899-12-31 | 0.875 | 0.875 | 0.95833 | 1899-12-31
KANO INDUSTRIAL | KUMBOTSO | SHARADA | 33KV BATA | A | 0.83333 | 20 | 19.5 | 1900-01-29 | 68400 | 1900-01-24 | 0
KANO INDUSTRIAL | KUMBOTSO | DORAYI | 33KV ATM | A | 0.83333 | 20 | 6.7 | 1900-01-28 16:21 | 27500 | 1900-01-24 | 1900-01-26 18:35 | 0.94097 | 1899-12-31 | 0.51736 | 0.97639 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.45347 | 0.95833 | 0.99514 | 0.61042 | 0.96389 | 1899-12-31 | 0.62778 | 0.39792 | 0.95347 | 0.99653 | 0.72847 | 0.88125 | 1899-12-31 | 0.77292 | 1899-12-31
KANO INDUSTRIAL | KUMBOTSO | AKTH | 33KV SPANISH 1 | A | 0.83333 | 20 | 0 | 1900-01-29 | 37000 | 1900-01-24 | 1900-01-26 22:00 | 0.70833 | 1899-12-31 | 0.54167 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.41667 | 1899-12-31 | 1899-12-31 | 0.58333 | 1899-12-31 | 1899-12-31 | 0.58333 | 0.41667 | 0.70833 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 1899-12-31
KANO INDUSTRIAL | KUMBOTSO | ZOO ROAD | 33KV SPANISH 2 | A | 0.83333 | 20 | 0.8 | 1900-01-28 02:29 | 40000 | 1900-01-24 | 1900-01-24 20:28 | 0.57083 | 0.82222 | 0.81597 | 0.89722 | 1899-12-31 | 0.77778 | 0.84236 | 0.89306 | 0.84722 | 0.89514 | 0.85069 | 0.79167 | 0.95833 | 0.88542 | 0.90417 | 0.95833 | 1899-12-31 | 0.77847 | 0.73194 | 0.525 | 0.94444 | 0.73542 | 0.60556 | 0.91111 | 0.81806 | 0.97569 | 0.59653 | 0.53958 | 0.98056 | 1899-12-31 | 1899-12-31
KANO INDUSTRIAL | DANAGUNDI | AKTH | 33KV ZARIA ROAD | A | 0.83333 | 20 | 20.4 | 1900-01-27 22:33 | 12100 | 1900-01-24 | 1900-01-21 15:58 | 0.65903 | 0.26389 | 0.71597 | 0.58333 | 0.81042 | 0 | 0.55069 | 0.7375 | 0.47361 | 0.72778 | 0.225 | 0.91667 | 0.96944 | 0.92639 | 0.92986 | 0.89931 | 0.75764 | 0.47917 | 0.94097 | 0.5625 | 0.94306 | 0.92014 | 0.60833 | 0.94583 | 0.86944 | 0.96319 | 0.64861 | 0.86736 | 0.9125 | 0.91389 | 0.94375
KANO CENTRAL | DANAGUNDI | BADAWA | 33KV CLUB | A | 0.83333 | 20 | 18.8 | 1900-01-27 22:49 | 82950 | 1900-01-24 | 1900-01-21 09:12 | 0.87222 | 0.76181 | 0.40417 | 0.73333 | 0.93819 | 0.57292 | 0.19861 | 0.41667 | 0.27222 | 0.92569 | 0.5 | 0.60764 | 0.60764 | 0.97847 | 1899-12-31 | 0.59861 | 0.96806 | 0.46875 | 1899-12-31 | 0.47639 | 0.82361 | 1899-12-31 | 0.59167 | 0.66875 | 0.575 | 0.93403 | 0.77014 | 1899-12-31 | 0.83056 | 0.94653 | 0.94167
KANO CENTRAL | DANAGUNDI | KEDCO HQ | 33KV CBN | A | 0.83333 | 20 | 9.8 | 2022-12-07 05:33 | 71640 | 1900-01-24 | 1900-01-24 18:43 | 0.91667 | 0.875 | 0.91667 | 0.85278 | 0.67708 | 0.89306 | 0.6125 | 0.90278 | 0.44792 | 0.91667 | 0.875 | 0.76806 | 0.97917 | 0.78056 | 0.96667 | 0.81597 | 0.75625 | 0.33889 | 0.96597 | 0.66042 | 0.90833 | 0.87083 | 0.59792 | 0.92014 | 0.99236 | 0.91458 | 0.81042 | 0.9875 | 0.95972 | 0.90764 | 0.99236
KANO NORTH | DANAGUNDI | RIJIYAR ZAKI | 33KV BUK | A | 0.83333 | 20 | 20.7 | -6601869.7424 | 70200 | 1900-01-24 | 1900-01-13 10:34 | 0.39028 | 0.18958 | 0.39167 | 0.10694 | 0.29167 | 0.82639 | 0.17569 | 0.31181 | 0.375 | 0.375 | 0.875 | 0.52222 | 0.32986 | 0.67569 | 0.6125 | 0.47361 | 0.58542 | 0.21736 | 0.50139 | 0.35486 | 0.48333 | 0.52569 | 0.11181 | 0.65694 | 0.42222 | 0.54167 | 0.54931 | 0.4625 | 0.62639 | 0.76319 | 0.71528
KANO NORTH | DANAGUNDI | KANO CITY | 33KV KURNA | A | 0.83333 | 20 | 20.4 | 2022-11-05 14:57 | 126449 | 1900-01-24 | 1900-01-14 14:20 | 0.56042 | 0.38194 | 0.85694 | 0.39792 | 0.54167 | 0.51597 | 0.1625 | 0.30556 | 0.3125 | 0.38819 | 0.59306 | 0.64167 | 0.097917 | 0.33958 | 0.22083 | 0.47153 | 0.79306 | 0.33889 | 0.66181 | 0.22847 | 0.84375 | 0.73958 | 0.35417 | 0.71528 | 0.44653 | 0.80278 | 0.12847 | 0.66181 | 0.48472 | 0.62639 | 0.98333
KANO NORTH | DANAGUNDI/BUKAVU | RIJIYAR ZAKI | 33KV DAWANAU | E | 0.16667 | 4 | 4.5 | 2022-09-10 10:56 | 21865 | 1900-01-04 | 1900-01-01 10:19 | 0 | 0 | 0.375 | 0 | 0.041667 | 0.0090278 | 0.027778 | 0 | 0 | 0.083333 | 0.125 | 0.25 | 0 | 0.032639 | 0 | 0.013889 | 0.022222 | 0.13194 | 0.33403 | 0.15972 | 0.061806 | 0 | 0 | 0.41528 | 0.023611 | 0.18194 | 0 | 0 | 0.015972 | 0 | 0.125
KANO NORTH | DANAGUNDI | KANO CITY | 33KV DAN AGUNDI 1 | A | 0.83333 | 20 | 9.8 | 1900-01-29 | 42745 | 1900-01-24 | 1900-01-20 07:23 | 1899-12-31 | 0.5625 | 0.34722 | 0.775 | 0.27986 | 0.58333 | 0.925 | 0.43056 | 0.35069 | 0.93264 | 0.70833 | 1899-12-31 | 1899-12-31 | 0.89931 | 0.85903 | 0.775 | 0.93542 | 0.47083 | 0.81806 | 0.51458 | 0.46458 | 0.79931 | 0.42639 | 0.78542 | 0.56944 | 0.80764 | 0.49306 | 0.60694 | 0.57222 | 0.64444 | 0.97083
KANO NORTH | DANAGUNDI | KANO CITY | 33KV DAN AGUNDI 2 | B | 0.66667 | 16 | 8 | 1900-01-29 | 24100 | 1900-01-19 | 1900-01-18 09:24 | 0.59167 | 0.94931 | 0.40278 | 0.60833 | 0.39306 | 0.61528 | 0.16736 | 0.65139 | 0.33333 | 0.81458 | 0.65278 | 0.83333 | 1899-12-31 | 0.94097 | 0.76944 | 0.88819 | 0.97083 | 0.33472 | 0.60833 | 0.43472 | 0.40139 | 0.55694 | 0.44931 | 0.70139 | 0.58472 | 0.44514 | 0.725 | 0.86389 | 0.35139 | 0.65347 | 0.69861
KANO NORTH | KUMBOTSO | RIJIYAR ZAKI | 33KV RIJIYAR ZAKI | A | 0.83333 | 20 | 14.8 | 1900-01-27 11:54 | 31400 | 1900-01-24 | 1900-01-11 17:30 | 0.60556 | 0.43403 | 0.54167 | 0.073611 | 0.30764 | 0.78403 | 0.23611 | 0.40069 | 0.95833 | 0.64792 | 0.97917 | 0.51875 | 0 | 0 | 0.49028 | 0.43681 | 0.10833 | 0.20833 | 0.56597 | 0.35139 | 0.17361 | 0.58889 | 0.38472 | 0.71667 | 0.43611 | 0.36458 | 0.10833 | 0 | 0.14097 | 0.64444 | 0.52222
KANO CENTRAL | DAKATA | SABON GARI | 33KV IDH | A | 0.83333 | 20 | 20.3 | 1900-01-27 10:01 | 67550 | 1900-01-24 | 1900-01-17 15:26 | 0.61319 | 0.45833 | 0.4875 | 0.5 | 0.41319 | 0.45833 | 0.45833 | 0.65556 | 0.61528 | 0.93056 | 0.60694 | 0.57569 | 0.32778 | 0.60764 | 0.63681 | 0.81042 | 0.72917 | 0.45417 | 0.83333 | 0.55694 | 0.70972 | 0.69583 | 0.48681 | 0.76458 | 0.47153 | 0.60069 | 0.58125 | 0.44861 | 0.69306 | 0.48681 | 0.975
KANO CENTRAL | DAKATA | BOMPAI | 33KV FLOUR MILLS | A | 0.83333 | 20 | 14 | 1900-01-28 22:31 | 105575 | 1900-01-24 | 1900-01-24 10:14 | 0.80556 | 0.79167 | 0.69375 | 0.43542 | 1899-12-31 | 0.88472 | 0.81597 | 0.58333 | 0.76319 | 1899-12-31 | 0.5 | 0.76042 | 0.76042 | 0.99167 | 0.88403 | 0.99444 | 0.88889 | 0.42917 | 0.97708 | 0.7125 | 0.98264 | 0.83264 | 0.60694 | 1899-12-31 | 1899-12-31 | 0.86389 | 0.825 | 1899-12-31 | 1899-12-31 | 0.80139 | 0.84167
KANO CENTRAL | DAKATA | BOMPAI | 33KV MTN | A | 0.83333 | 20 | 14 | 1900-01-27 11:03 | 56565 | 1900-01-24 | 1900-01-22 00:43 | 0.74861 | 0.63958 | 0.57569 | 0.63681 | 0.57778 | 0.57778 | 0.84722 | 0.57569 | 0.875 | 1899-12-31 | 0.77014 | 0.73194 | 0.48264 | 0.95347 | 0.87847 | 0.84861 | 0.65903 | 0.47292 | 0.90417 | 0.48472 | 0.975 | 0.91667 | 0.57986 | 0.75417 | 0.98125 | 0.71944 | 0.59653 | 0.94653 | 0.62361 | 0.70417 | 0.99236
KANO CENTRAL | DAKATA | BOMPAI | 33KV SMALL SCALE | A | 0.83333 | 20 | 9.1 | #VALUE! | 61100 | 1900-01-24 | 1900-01-12 23:40 | 0.55694 | 0.45069 | 0.24167 | 0.69028 | 0.24028 | 0.39722 | 0.48958 | 0.083333 | 0.46806 | 0.54167 | 0.51736 | 0.34375 | 0.66667 | 0.3875 | 0.37361 | 0.60486 | 0.84306 | 0.55625 | 0.3 | 0.14028 | 0.39167 | 0.56806 | 0.26389 | 0.48472 | 0.38611 | 0.29167 | 0.21944 | 0.61528 | 0.41181 | 0.71528 | 0.74514
KANO EAST | DAKATA/SMALL SCALE | KAWAJI | 33KV GEZAWA | E | 0.16667 | 4 | 4.3 | 1900-01-26 22:22 | 46100 | 1900-01-04 | 1900-01-07 23:59 | 0.49583 | 0.020139 | 0.15486 | 0.425 | 0.20833 | 0.27014 | 0.35833 | 0.083333 | 0.29167 | 0.43611 | 0.48333 | 0.27014 | 0.5 | 0.11944 | 0.34097 | 0.54375 | 0.28958 | 0.20833 | 0.29722 | 0.047917 | 0.052778 | 0.325 | 0.26389 | 0.19722 | 0.25417 | 0.083333 | 0 | 0.16111 | 0.37986 | 0.7125 | 0.725
KANO EAST | DAKATA | KAWAJI | 33KV GASKIYA | A | 0.83333 | 20 | 17 | 2390-07-10 17:57 | 86550 | 1900-01-24 | 1900-01-19 11:17 | 0.65417 | 0.40556 | 0.54167 | 0.26806 | 0.70833 | 0.5 | 0.58333 | 0.74236 | 0.65903 | 0.89931 | 0.64653 | 0.82083 | 0.80417 | 0.93264 | 0.80069 | 0.7875 | 0.75625 | 0.45972 | 0.88958 | 0.57917 | 0.71944 | 0.76528 | 0.5125 | 0.83472 | 0.69514 | 0.44861 | 0.475 | 0.78542 | 0.67708 | 0.47639 | 0.64167
KANO EAST | DAKATA | KAWAJI | 33KV JODA | A | 0.83333 | 20 |  | 2022-09-06 22:36 |  | 1900-01-24 | 1900-01-22 13:00 | 0.45833 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.83333 | 1899-12-31 | 1899-12-31 | 0.625 | 0.75 | 1899-12-31 | 0.33333 | 1899-12-31 | 0.66667 | 1899-12-31 | 1899-12-31 | 0.375 | 0.91667 | 0.45833 | 0.91667 | 0.83333 | 0.41667 | 0 | 0 | 0
KANO EAST | DAKATA | HOTORO | 33KV NNPC | A | 0.83333 | 20 | 20 | 2022-09-08 02:45 | 20200 | 1900-01-24 | 1900-01-17 06:18 | 0.62014 | 0.5 | 0.31667 | 0.625 | 0.25 | 0.22569 | 0.57778 | 0.75 | 0.68125 | 0.63542 | 0.58333 | 0.54167 | 0.375 | 0.84583 | 0.49583 | 0.66319 | 0.84028 | 0.52292 | 0.70347 | 0.45833 | 0.70417 | 0.74722 | 0.35069 | 0.73611 | 0.65972 | 0.66458 | 0.34444 | 0.65417 | 0.72847 | 0.55764 | 0.90347
KANO EAST | DAKATA | HOTORO | 33KV LADANAI |  | 0.5 | 12 |  | 1900-01-29 |  | 1900-01-14 | 1900-01-17 07:33 | 0.62014 | 0.5 | 0.31667 | 0.625 | 0.25 | 0.22569 | 0.57778 | 0.75 | 0.68125 | 0.63542 | 0.58333 | 0.54167 | 0.375 | 0.84583 | 0.49583 | 0.66319 | 0.84028 | 0.52292 | 0.70694 | 0.45833 | 0.70417 | 0.74722 | 0.35069 | 0.73611 | 0.70833 | 0.66458 | 0.34444 | 0.65417 | 0.72847 | 0.55764 | 0.90347
KANO EAST | DAKATA/MARIRI | WUDIL | 33KV MAKOLE | C | 0.5 | 12 | 0 | 1900-01-29 | 8000 | 1900-01-14 | 1900-01-14 07:26 | 0.48333 | 0 | 0.89444 | 0.20833 | 0.29167 | 0.35903 | 0.64236 | 0.61528 | 0.75 | 0.65903 | 0.66667 | 0.68958 | 0.49236 | 0.66181 | 0.76875 | 0.35417 | 0.17083 | 0.27222 | 1899-12-31 | 0.12222 | 0.43542 | 0.14514 | 0.35 | 0.64861 | 0.45833 | 0.88819 | 0.75139 | 0.44375 | 0.30972 | 0.35347 | 0.42361
KANO EAST | WUDIL TS | WUDIL | 33KV WUDIL | A | 0.83333 | 20 | 5.8 | 2022-09-07 06:29 | 18100 | 1900-01-24 | 1900-01-24 11:56 | 1899-12-31 | 1899-12-31 | 0.91667 | 0.91667 | 0.91667 | 0.85486 | 0.74583 | 0.91667 | 0.80764 | 0.875 | 0.66667 | 0.97917 | 0.975 | 0.98889 | 0.92708 | 0.93403 | 0.69236 | 0 | 1899-12-31 | 0.625 | 0.80833 | 0.87431 | 0.58819 | 0.91597 | 0.86667 | 0.94583 | 0.66667 | 0.54167 | 0.82083 | 0.99097 | 0.73958
KANO EAST | WUDIL TS | WUDIL | 33KV GANO | C | 0.5 | 12 | 17.7 | 2022-09-08 10:14 | 11950 | 1900-01-14 | 1900-01-15 07:16 | 0.48333 | 1899-12-31 | 0.89444 | 0.20833 | 0.29167 | 0.35903 | 0.64236 | 0.61528 | 0.75 | 0.65903 | 0.66667 | 0.68958 | 0.49236 | 0.66181 | 0.76875 | 0.35417 | 0.17083 | 0.27222 | 1899-12-31 | 0.12222 | 0.43542 | 0.14514 | 0.35 | 0.64861 | 0.45139 | 0.88819 | 0.75139 | 0.44375 | 0.30972 | 0.35347 | 0.42361
KANO EAST | WUDIL TS | WUDIL | 33KV GARKO | E | 0.16667 | 4 | 3.8 | 2022-09-05 22:51 |  | 1900-01-04 | 1900-01-07 11:00 | 0.29167 | 0.083333 | 0.16667 | 0.54167 | 0.58333 | 0.33333 | 0.41667 | 0.29167 | 0.25 | 0.16667 | 0.33333 | 0.58333 | 0.54167 | 0.45833 | 0.083333 | 0.25 | 0 | 0.29167 | 0.29167 | 0 | 0.33333 | 0.25 | 0 | 0.29167 | 0.29167 | 0.29167 | 0.25 | 0.25 | 0.33333 | 0.041667 | 0.16667
KANO EAST | WUDIL/WUDIL | WUDIL | 33KV GAYA | E | 0.16667 | 4 | 2.3 | 1900-01-23 20:37 | 11700 | 1900-01-04 | 1900-01-06 08:15 | 0.063194 | 0.16667 | 0.16667 | 0.29167 | 0.34375 | 0.33333 | 0.0069444 | 0.24097 | 0.26389 | 0.27083 | 0.29167 | 0.16667 | 0.58333 | 0.67083 | 0 | 0.09375 | 0.22569 | 0.38542 | 0.16667 | 0.041667 | 0.51667 | 0.5625 | 0 | 0.15347 | 0 | 0.40972 | 0.125 | 0.16667 | 0.14236 | 0.36111 | 0.13264
JIGAWA SOUTH | DUTSE | DUTSE | 33KV SUMAILA | D | 0.33333 | 8 | 2.3 | 2145-02-13 05:46 | 20800 | 1900-01-09 | 1900-01-13 04:56 | 0.66667 | 0.56528 | 0.10694 | 0.5 | 0.18056 | 0.44375 | 0.40764 | 0.54167 | 0.56597 | 0.28194 | 0.38472 | 0.33333 | 0.45486 | 0.59653 | 0.45833 | 0.83542 | 0.22986 | 0.22986 | 0.44583 | 0.47708 | 0.62917 | 0.32014 | 0.59167 | 0.63125 | 0.40278 | 0.50556 | 0.54653 | 0.43264 | 0.58542 | 0.32222 | 0.53194
KANO WEST | KUMBOTSO | MAIKALWA | 33KV BAGAUDA | D | 0.33333 | 8 | 11.3 | 1900-01-23 04:08 | 41600 | 1900-01-09 | 1900-01-11 13:00 | 0.25 | 0.375 | 0.375 | 0.125 | 0.5 | 0.375 | 0.33333 | 0.45833 | 0.41667 | 0.41667 | 0.54167 | 0.41667 | 0.54167 | 0.45833 | 0.625 | 0.29167 | 0.41667 | 0.54167 | 0.375 | 0.29167 | 0.54167 | 0.375 | 0.041667 | 0.5 | 0.25 | 0.375 | 0.41667 | 0.75 | 0.5 | 0.125 | 0.54167
KANO WEST | DANAGUNDI/ZARIA ROAD | MAIKALWA | 33KV DAWAKI |  | 0.5 | 12 |  | 1900-01-28 15:49 |  | 1900-01-14 | 1900-01-22 07:39 | 0.625 | 0.26667 | 0.70833 | 0.58333 | 0.69306 | 1899-12-31 | 0.55069 | 0.67361 | 0.47361 | 0.76389 | 0.94653 | 0.875 | 0.96944 | 0.92639 | 0.92986 | 0.89792 | 0.75556 | 0.47847 | 0.85833 | 0.5625 | 0.94306 | 0.48056 | 0.60069 | 0.9625 | 0.95417 | 0.96181 | 0.60208 | 0.44444 | 0.92014 | 0.93194 | 0.97917
KANO WEST | DANGORA | KWANAR DANGORA | 33KV LAW SCHOOL | D | 0.33333 | 8 | 12.3 | 1900-01-27 05:56 | 18750 | 1900-01-09 | 1900-01-18 | 0.79167 | 0.91667 | 0.79167 | 0.54167 | 0.625 | 0.70833 | 0.70833 | 0 | 0.16667 | 0.16667 | 0 | 0.91667 | 0.95833 | 1899-12-31 | 0.75 | 0.375 | 0.25 | 0.79167 | 0.875 | 0.45833 | 0.83333 | 0.54167 | 0.54167 | 0.66667 | 0.75 | 0.66667 | 0.41667 | 0.54167 | 0.70833 | 0.70833 | 0.83333
KANO WEST | DANGORA | KWANAR DANGORA | 33KV KARAYE | E | 0.16667 | 4 | 6.3 | 1900-01-28 05:28 | 36400 | 1900-01-04 | 1900-01-21 19:00 | 0.66667 | 0.875 | 0.625 | 1899-12-31 | 0.70833 | 0.75 | 0.75 | 1899-12-31 | 0.375 | 0.375 | 0.91667 | 0.91667 | 0.58333 | 0.70833 | 0.70833 | 0.95833 | 0.83333 | 0.875 | 1899-12-31 | 0.45833 | 0.54167 | 0.66667 | 0.54167 | 0.875 | 1899-12-31 | 0.45833 | 0.70833 | 0.875 | 0.70833 | 0.70833 | 0.625
KANO WEST | DANGORA | KWANAR DANGORA | 33KV FALGORE | E | 0.16667 | 4 | 5.1 | 1900-01-26 04:35 | 20300 | 1900-01-04 | 1900-01-21 14:00 | 1899-12-31 | 0.875 | 0.083333 | 0.54167 | 1899-12-31 | 0.70833 | 0.70833 | 0.33333 | 0.375 | 0.375 | 1899-12-31 | 0.625 | 0.95833 | 0.91667 | 1899-12-31 | 0.79167 | 0.91667 | 0.875 | 1899-12-31 | 0.375 | 0.91667 | 0.75 | 0.54167 | 0.66667 | 0.91667 | 0.58333 | 0.41667 | 0.625 | 0.875 | 0.83333 | 1899-12-31
KANO WEST | TAMBURAWA | PANSHEKARA | 33KV KWANKWASO | E | 0.16667 | 4 | 8.7 | 1900-01-24 22:00 | 23850 | 1900-01-04 | 1900-01-11 00:39 | 0.875 | 0.33333 | 0.41667 | 0.5 | 0.30556 | 0.47431 | 0.47431 | 0.39792 | 0.5 | 0.375 | 0.625 | 0.31944 | 0.58333 | 0.39792 | 0.35625 | 0.41667 | 0.37708 | 0.16667 | 0.38264 | 0.125 | 0.29167 | 0.45833 | 0.41667 | 0.25 | 0.45833 | 0.45833 | 0.29167 | 0.25 | 0.20833 | 0.54167 | 0
KANO INDUSTRIAL | TAMBURAWA | SHARADA | 33KV COCA COLA | A | 0.83333 | 20 | 20.7 | 1900-01-28 21:50 | 66550 | 1900-01-24 | 1900-01-26 01:10 | 0.45833 | 0.91667 | 1899-12-31 | 0.91667 | 1899-12-31 | 0.77778 | 0.77778 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.92917 | 1899-12-31 | 1899-12-31 | 0.85764 | 1899-12-31 | 0.83333 | 0.43264 | 0.69028 | 0.58333 | 1899-12-31 | 0.91667 | 0.625 | 0.91667 | 0.83333 | 0.83333 | 1899-12-31 | 1899-12-31 | 0.91667 | 0.91667 | 0.91667
KANO WEST | TAMBURAWA | PANSHEKARA | 33KV CHALAWA WATER WORKS |  | 0.5 | 12 | 6.2 | 1900-01-29 | 11300 | 1900-01-14 | 1900-01-26 10:53 | 0.92639 | 0.78125 | 1899-12-31 | 0.5 | 1899-12-31 | 1899-12-31 | 0.56597 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.98819 | 0.875 | 1899-12-31 | 0.96806 | 0.85417 | 1899-12-31 | 0.85625 | 0.875 | 0.92153 | 0.54306 | 0.9375 | 0.57708 | 0.58542 | 1899-12-31 | 0.92014 | 0.98889 | 0.99097 | 1899-12-31 | 0.89931 | 0.89931 | 1899-12-31
KANO WEST | TAMBURAWA | MAIKALWA | 33KV TAMBURAWA WATER WORKS | A | 0.83333 | 20 | 4.8 | 1900-01-29 | 23400 | 1900-01-24 | 1900-01-22 20:53 | 0.49167 | 0.64583 | 0.79931 | 0.85417 | 0.63194 | 0.98958 | 0.98958 | 0.94444 | 0.875 | 0.86389 | 0.93889 | 0.85417 | 0.99028 | 0.94444 | 0.85278 | 0.98681 | 0.69097 | 0.3875 | 0.89931 | 0.51667 | 0.95833 | 0.30764 | 0.21528 | 0.92361 | 0.65278 | 0.77708 | 0.73333 | 0.61319 | 0.94861 | 0.84306 | 0.75
KANO WEST | TAMBURAWA/TAM. W/PLANT | MAIKALWA | 33KV DR JAMIL GWAMNA | A | 0.83333 | 20 | 2.7 | 1900-01-29 | 16400 | 1900-01-24 | 1900-01-21 05:34 | 0.49167 | 0.64583 | 0.59722 | 0.85417 | 0.63194 | 0.98958 | 0.98958 | 0.94097 | 0.875 | 0.86389 | 0.93889 | 0.85417 | 0.99028 | 0.94097 | 0.85069 | 0.79167 | 0.2375 | 0.22222 | 0.89583 | 0.51389 | 0.95833 | 0.28333 | 0.21528 | 0.71528 | 0.63889 | 0.77083 | 0.65694 | 0.34375 | 0.94444 | 0.83889 | 0.75
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV HADEJIA | A | 0.83333 | 20 | 5.5 | 1900-01-27 12:57 | 24850 | 1900-01-24 | 1900-01-24 05:24 | 0.83333 | 0.95833 | 1899-12-31 | 0.93542 | 0.99306 | 0.97222 | 0.39583 | 0.66667 | 0.66667 | 0.98403 | 0.98403 | 0.81528 | 0.85556 | 0.875 | 0.75 | 1899-12-31 | 1899-12-31 | 0.10903 | 1899-12-31 | 0.64931 | 0.97917 | 1899-12-31 | 0.425 | 0.58333 | 1899-12-31 | 1899-12-31 | 0.76181 | 1899-12-31 | 0.79167 | 0.55764 | 0.68264
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV BIRNIWA | D | 0.33333 | 8 | 1.7 | 1900-03-25 12:53 | 10525 | 1900-01-09 | 1900-01-15 20:00 | 0.83333 | 0.58333 | 0.625 | 0.625 | 0.5 | 0.41667 | 0.5 | 0.95833 | 0.95833 | 0.79167 | 0.79167 | 0.16667 | 0.33333 | 0.375 | 0.33333 | 1899-12-31 | 0.79167 | 0.083333 | 0.33333 | 0 | 0.41667 | 0.54167 | 0.29167 | 0.54167 | 0.625 | 0.54167 | 0.25 | 0.41667 | 0.875 | 0.375 | 0.95833
JIGAWA NORTH | HADEJIA | GUMEL | 33KV GUMEL | D | 0.33333 | 8 | 4.9 | 1900-03-27 08:39 | 33050 | 1900-01-09 | 1900-01-09 00:23 | 0.77361 | 0.80347 | 0.58333 | 0.69097 | 0.73958 | 0.58333 | 0.33333 | 0.80347 | 0.94167 | 0.60764 | 0.64097 | 0.34931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44861 | 0.7375 | 0.97917
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV KAFIN HAUSA | A | 0.83333 | 20 | 5.9 | 1900-01-29 06:39 | 21300 | 1900-01-24 | 1900-01-25 00:32 | 0.89792 | 0.98889 | 1899-12-31 | 0.95833 | 0.88403 | 0.71528 | 0.58333 | 0.82014 | 0.375 | 0.33333 | 0.82361 | 0.97917 | 0.97917 | 0.77569 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.27153 | 0.92361 | 0.59514 | 0.84028 | 1899-12-31 | 0.625 | 1899-12-31 | 1899-12-31 | 0.93403 | 0.80208 | 1899-12-31 | 0.91667 | 1899-12-31 | 1899-12-31
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV YANLEMAN | D | 0.33333 | 8 |  | 1900-01-29 |  | 1900-01-09 | 1900-01-24 18:39 | 0.89792 | 0.98889 | 1899-12-31 | 0.95833 | 0.88403 | 0.71528 | 0.58333 | 0.82014 | 0.375 | 0.33333 | 0.82361 | 0.97917 | 0.97917 | 0.77569 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.27153 | 0.92361 | 0.59514 | 0.59514 | 1899-12-31 | 0.625 | 1899-12-31 | 1899-12-31 | 0.93403 | 0.80208 | 1899-12-31 | 0.91667 | 1899-12-31 | 1899-12-31
JIGAWA NORTH | HADEJIA | HADEJIA | 33KV UNIVERSITY | A | 0.83333 | 20 |  | 1900-01-29 |  | 1900-01-24 | 1900-01-21 03:00 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.41667 | 0.41667 | 0.70833 | 0 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0 | 0.25 | 1899-12-31 | 0 | 0.58333 | 0.625 | 0 | 0.375 | 1899-12-31 | 1899-12-31 | 0.79167 | 0.25 | 0.83333 | 1899-12-31 | 0.875
JIGAWA NORTH | GAGARAWA | GUMEL | 33KV RICE MILLS | A | 0.83333 | 20 |  | 1900-01-29 |  | 1900-01-24 | 1900-01-28 14:56 | 1899-12-31 | 0.98472 | 1899-12-31 | 0.81806 | 1899-12-31 | 0.89444 | 1899-12-31 | 1899-12-31 | 0.98194 | 0.98194 | 1899-12-31 | 1899-12-31 | 0.98333 | 0.98472 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.36806 | 1899-12-31 | 0.625 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31
JIGAWA NORTH | GAGARAWA | GUMEL | 33KV GAGARAWA | B | 0.66667 | 16 |  | 1900-01-28 15:40 |  | 1900-01-19 | 1900-01-28 13:33 | 0.95833 | 0.98472 | 0.83333 | 0.95833 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.98194 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.98333 | 0.98472 | 0.97014 | 1899-12-31 | 1899-12-31 | 0.36806 | 1899-12-31 | 0.625 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 1899-12-31
JIGAWA NORTH | GAGARAWA | GUMEL | 33KV GUJUNGU | D | 0.33333 | 8 |  | 1900-01-28 12:19 |  | 1900-01-09 | 1900-01-28 14:56 | 1899-12-31 | 0.98472 | 1899-12-31 | 0.81806 | 1899-12-31 | 0.89444 | 1899-12-31 | 1899-12-31 | 0.98194 | 0.98194 | 1899-12-31 | 1899-12-31 | 0.98333 | 0.98472 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.36806 | 1899-12-31 | 0.625 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31
JIGAWA SOUTH | DUTSE | BIRNIN KUDU | 33KV BIRNIN KUDU | B | 0.66667 | 16 | 7.7 | 1900-01-26 14:43 | 24450 | 1900-01-19 | 1900-01-14 20:45 | 0.81319 | 0.30278 | 0.72917 | 0.20833 | 0.29167 | 0.33333 | 0.39583 | 0.75 | 0.61111 | 0.60069 | 0.26111 | 0.47986 | 0.46875 | 0.23542 | 0.46667 | 0.37569 | 0.83889 | 0.83889 | 0.30903 | 0.47708 | 0.44514 | 0.25694 | 0.56042 | 0.59306 | 0.53403 | 0.44514 | 0.76806 | 0.92361 | 0.37569 | 0.32917 | 0.84583
JIGAWA SOUTH | DUTSE | DUTSE | 33KV JAHUN | D | 0.33333 | 8 | 5.7 | 2267-09-19 10:37 | 16700 | 1900-01-09 | 1900-01-10 14:14 | 0.58333 | 0.27778 | 0.25 | 0.3875 | 0.35278 | 0.23681 | 0.25 | 0.625 | 0.51875 | 0.51667 | 0.29167 | 0.15764 | 0.35764 | 0.29792 | 0.21875 | 0.17847 | 0.82292 | 0.82292 | 0.43611 | 0.13472 | 0.4875 | 0.14375 | 0.57431 | 0.59306 | 0.12431 | 0.20208 | 0.24861 | 0.40486 | 0.43472 | 0.18056 | 0.48194
JIGAWA SOUTH | DUTSE | DUTSE | 33KV DUTSE | A | 0.83333 | 20 | 7.8 | 1900-01-28 05:59 | 38900 | 1900-01-24 | 1900-01-25 20:16 | 0.83333 | 1899-12-31 | 1899-12-31 | 0.83333 | 1899-12-31 | 0.75 | 0.83333 | 0.80972 | 0.92847 | 0.5 | 0.92847 | 0.95069 | 0.83333 | 0.91111 | 0.79653 | 1899-12-31 | 0.64167 | 0.64167 | 0.89306 | 0.62431 | 1899-12-31 | 0.85556 | 0.59167 | 1899-12-31 | 0.77153 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV AJIWA WATER WORKS | A | 0.83333 | 20 | 7.1 | 2016-09-01 17:16 | 47800 | 1900-01-24 | 1900-01-25 11:06 | 0.875 | 0.58333 | 0.625 | 0.21875 | 1899-12-31 | 0.875 | 0.70833 | 1899-12-31 | 0.79167 | 1899-12-31 | 0.83333 | 0.875 | 0.95833 | 0.95833 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.83333 | 1899-12-31 | 0.64375 | 0.79167 | 0.91667 | 0.6 | 0.95833 | 1899-12-31 | 0.95833 | 0.83333 | 0.83333 | 1899-12-31 | 1899-12-31 | 0.83333
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV POWER HOUSE | A | 0.83333 | 20 | 24.9 | 1900-01-29 | 94600 | 1900-01-24 | 1900-01-28 16:01 | 0.95833 | 1899-12-31 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.875 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.79167 | 1899-12-31 | 0.54236 | 1899-12-31 | 1899-12-31 | 0.625 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV POLYTECHNIC | D | 0.33333 | 8 | 5.2 | 1900-01-29 | 55500 | 1900-01-09 | 1900-01-21 20:02 | 0.79167 | 0.54167 | 0.875 | 0.75 | 0.70833 | 0.41667 | 0.70833 | 1899-12-31 | 1899-12-31 | 0.91667 | 0.91667 | 0.91667 | 0.875 | 0.91667 | 0.91667 | 1899-12-31 | 0.875 | 0.58333 | 0.83333 | 0.20833 | 0.70833 | 1899-12-31 | 0.5 | 0.5 | 0.45833 | 0.29236 | 0.83333 | 0.83333 | 0.54236 | 0.625 | 0.79167
KATSINA NORTH | KATSINA | KATSINA CITY | 33KV KAITA | D | 0.33333 | 8 | 5.8 | 1900-01-28 18:25 | 29250 | 1900-01-09 | 1900-01-23 11:27 | 0.75 | 0.875 | 0.625 | 0.97917 | 0.54167 | 0.66667 | 0.70833 | 0.94583 | 1899-12-31 | 0.875 | 0.875 | 0.73333 | 0.79167 | 0.83333 | 0.45833 | 0.94792 | 1899-12-31 | 0.54167 | 0.75 | 0.39722 | 0.86806 | 0.95833 | 0.625 | 1899-12-31 | 0.67292 | 0.95833 | 0.875 | 0.75 | 0.76597 | 0.95833 | 0.75
KATSINA NORTH | KATSINA | KATSINA URBAN | 33KV DANA | A | 0.83333 | 20 | 0 | 1900-01-29 | 2500 | 1900-01-24 | 0
KATSINA NORTH | KATSINA | KATSINA CITY | 33KV KOFAR GUGA | A | 0.83333 | 20 | 11 | 1900-01-28 13:05 | 46650 | 1900-01-24 | 1900-01-22 19:53 | 0.97917 | 0.375 | 0.41667 | 0.375 | 0.875 | 0.95833 | 0.45833 | 0.625 | 0.95833 | 0.83333 | 0.875 | 0.875 | 1899-12-31 | 0.95833 | 0.375 | 0.375 | 1899-12-31 | 0.625 | 0.95833 | 0.625 | 0.88542 | 1899-12-31 | 0.625 | 0.51597 | 0.875 | 0.875 | 0.98958 | 0.875 | 1899-12-31 | 1899-12-31 | 0.66667
KATSINA NORTH | DAURA | DAURA | 33KV DAURA | A | 0.83333 | 20 | 8 | 1900-01-29 | 22700 | 1900-01-24 | 1900-01-28 19:00 | 0.95833 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.875 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 0.875 | 0.625 | 1899-12-31 | 1899-12-31 | 0.58333 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31
KATSINA NORTH | DAURA | DAURA | 33KV MASHI | C | 0.5 | 12 | 2.8 | 1900-01-26 10:17 | 16050 | 1900-01-14 | 1900-01-14 14:00 | 0.95833 | 0.54167 | 0.625 | 0.58333 | 0.5 | 0.375 | 0.29167 | 0.41667 | 0.75 | 0.66667 | 0.70833 | 0.625 | 0.875 | 0.083333 | 0.083333 | 0.375 | 0.5 | 0.54167 | 0.70833 | 0.20833 | 0.375 | 0.083333 | 0.125 | 0 | 0.95833 | 0.41667 | 0.33333 | 0.625 | 0.5 | 0.95833 | 0.79167
KATSINA NORTH | DAURA | DAURA | 33KV MAI ADUA | E | 0.16667 | 4 | 5.4 | 2022-09-05 08:39 | 18300 | 1900-01-04 | 1900-01-17 16:00 | 0.41667 | 0.875 | 0.5 | 0.625 | 0.91667 | 0.375 | 0.29167 | 0.625 | 0.70833 | 0.75 | 0.79167 | 0.66667 | 0.5 | 0.625 | 0.5 | 0.875 | 0.75 | 0.54167 | 0.70833 | 0.25 | 0.58333 | 0.875 | 0.16667 | 0.41667 | 0.41667 | 0.66667 | 0.45833 | 0.58333 | 0.91667 | 0.79167 | 0.5
KATSINA CENTRAL | DAURA | KANKIA | 33KV KAZAURE | C | 0.5 | 12 | 3.4 | 1900-01-28 09:52 | 21810 | 1900-01-14 | 1900-01-19 01:01 | 0.80486 | 0.3875 | 0.72847 | 0.71875 | 0.59444 | 0.55833 | 0.51736 | 0.41667 | 0.66667 | 0.5 | 0.93403 | 0.41667 | 0.47708 | 0.32778 | 0.64514 | 0.58194 | 0.83333 | 0.73958 | 0.70972 | 0.50903 | 1899-12-31 | 0.75 | 0.054861 | 0.95069 | 0.77222 | 0.48194 | 0.63819 | 0.98472 | 1899-12-31 | 0.80417 | 0.53819
KATSINA CENTRAL | KANKIA | KANKIA | 33KV DANBATTA | E | 0.16667 | 4 | 7.7 | 2022-09-01 23:59 |  | 1900-01-04 | 1900-01-08 20:06 | 0.041667 | 0.25 | 0.041667 | 0.041667 | 0.33333 | 0.083333 | 0.45833 | 0.58333 | 0.875 | 0.29167 | 0.54167 | 0.29167 | 0.41667 | 0.45833 | 0.5 | 0.375 | 0.25 | 0.25 | 0.25 | 0.125 | 0.20833 | 0.125 | 0.16667 | 0.33333 | 0.29167 | 0.41667 | 0.62917 | 0.25 | 0.25 | 0.33333 | 0.375
KATSINA CENTRAL | KANKIA | KANKIA | 33KV AMPRI GLOBAL | A | 0.83333 | 20 | 0 | 1900-01-29 | 500 | 1900-01-24 | 1900-01-27 08:00 | 0.875 | 1899-12-31 | 0.95833 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.70833 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.95833 | 0.5 | 1899-12-31 | 0.58333 | 1899-12-31 | 1899-12-31 | 0.58333 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.70833 | 1899-12-31 | 1899-12-31 | 0.54167 | 1899-12-31
KATSINA CENTRAL | KANKIA | KANKIA | 33KV MUSAWA | D | 0.33333 | 8 | 13.8 | 2390-06-13 16:28 | 46350 | 1900-01-09 | 1900-01-14 08:00 | 0.91667 | 0.70833 | 1899-12-31 | 0.625 | 0.41667 | 0.29167 | 0.45833 | 0.75 | 0.54167 | 0.41667 | 0.75 | 0.66667 | 0.45833 | 0.70833 | 0.33333 | 0.45833 | 0.54167 | 0.16667 | 0.66667 | 0.29167 | 0.58333 | 0.41667 | 0.16667 | 0.375 | 0.41667 | 0.45833 | 0.20833 | 0.5 | 0.375 | 0.33333 | 0.33333
KATSINA CENTRAL | KANKIA | DUTSENMA | 33KV DUTSENMA | C | 0.5 | 12 | 11.5 | 2022-09-01 23:15 | 39850 | 1900-01-14 | 1900-01-24 05:00 | 0.75 | 0.83333 | 1899-12-31 | 1899-12-31 | 0.83333 | 0.91667 | 0.5 | 0.66667 | 0.75 | 0.875 | 0.70833 | 0.29167 | 0.95833 | 0.95833 | 0.79167 | 1899-12-31 | 1899-12-31 | 0.75 | 1899-12-31 | 0.66667 | 1899-12-31 | 0.91667 | 0.54167 | 0.83333 | 0.70833 | 0.875 | 1899-12-31 | 0.54167 | 0.75 | 0.91667 | 0.875
KATSINA CENTRAL | KANKIA | DUTSENMA | 33KV WATARI | A | 0.83333 | 20 |  | 2022-09-05 17:10 |  | 1900-01-24 | 1900-01-23 21:00 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.95833 | 1899-12-31 | 1899-12-31 | 0.875 | 1899-12-31 | 0.70833 | 0.79167 | 0.79167 | 0.58333 | 0.5 | 0.875 | 0.79167 | 0.79167 | 0.20833 | 0.66667 | 0.45833 | 0.625 | 1899-12-31 | 0.91667 | 1899-12-31 | 0.79167 | 0.29167 | 1899-12-31 | 0.33333 | 1899-12-31
KATSINA SOUTH | FUNTUA | MALUMFASHI | 33KV MALUMFASHI | D | 0.33333 | 8 | 10.5 | 2022-09-04 15:58 | 82115 | 1900-01-09 | 1900-01-09 16:10 | 0.5 | 0.33333 | 0.33333 | 0.41667 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.625 | 0.54167 | 0.25 | 0.625 | 0.13194 | 0.375 | 0.16667 | 0.29167 | 0.45833 | 0.25 | 0.16667 | 0.375 | 0.33333 | 0.375 | 0.041667 | 0.20833 | 0.33333 | 0.25 | 0.16667 | 0.33333 | 0.20833 | 0.125 | 0.45833
KATSINA SOUTH | FUNTUA | MALUMFASHI | 33KV MAMMAN NASIR | B | 0.66667 | 16 | 3.9 | 2268-01-15 02:45 |  | 1900-01-19 | 1900-01-11 22:54 | 0.52292 | 0.35208 | 0.059028 | 0.27083 | 0.66667 | 0.83333 | 0.375 | 0.71875 | 0.875 | 0.15694 | 0.40069 | 0.84722 | 0.034722 | 0.60556 | 0.58889 | 0.31736 | 0.56806 | 0.39236 | 0.48611 | 0.19514 | 0.22847 | 0.31458 | 0.0083333 | 0.49306 | 0.28125 | 0.53958 | 0.74097 | 0.37153 | 0.41319 | 0.28264 | 0.013889
KATSINA SOUTH | FUNTUA | FUNTUA | 33KV DANDUME | E | 0.16667 | 4 | 5.2 | 1900-01-28 14:56 | 30300 | 1900-01-04 | 1900-01-10 16:07 | 0.25 | 0.041667 | 0.16667 | 0.20833 | 0.83333 | 0.41667 | 0.70833 | 0.45833 | 0.375 | 0.5 | 0.5 | 0.20833 | 0.19236 | 0.66667 | 0.25 | 0.25 | 0.29167 | 0.625 | 0.375 | 0.16667 | 0.625 | 0.25 | 0.041667 | 0.41667 | 0.083333 | 0.375 | 0.60417 | 0.29167 | 0.125 | 0.45833 | 0.91667
KATSINA SOUTH | FUNTUA | FUNTUA | 33KV KATSINA ROAD | A | 0.83333 | 20 | 6 | 1900-01-29 | 28850 | 1900-01-24 | 1900-01-25 07:51 | 1899-12-31 | 1899-12-31 | 0.79167 | 1899-12-31 | 1899-12-31 | 0.97014 | 0.83333 | 0.85903 | 0.625 | 0.80278 | 1899-12-31 | 0.875 | 0.70833 | 0.60278 | 0.69236 | 0.88194 | 0.60486 | 0.87708 | 0.73056 | 0.375 | 0.83333 | 0.75 | 0.54167 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.97222 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31
KATSINA SOUTH | FUNTUA | FUNTUA | 33KV TEXTILE | A | 0.83333 | 20 | 10.2 | 2022-09-09 23:49 | 28900 | 1900-01-24 | 1900-01-24 09:25 | 1899-12-31 | 0.81667 | 0.85764 | 0.98611 | 1899-12-31 | 0.80347 | 1899-12-31 | 0.64028 | 0.875 | 0.89861 | 0.72222 | 1899-12-31 | 0.48264 | 0.5625 | 0.78125 | 0.91736 | 0.83194 | 0.90278 | 0.93403 | 0.47708 | 0.66736 | 0.65764 | 0.53264 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.875 | 0.56944 | 0.61111 | 1899-12-31 | 0.98958
KANO NORTH | 15MVA TR1 DAN AGUNDI | KANO CITY | 11KV KOFAR NASSARAWA | C | 0.5 | 12 | 4 | 1900-01-28 06:18 | 14300 | 1900-01-14 | 1900-01-15 02:22 | 0.75 | 0.51389 | 0.30278 | 0 | 0.38611 | 0.29167 | 0.67708 | 0.31181 | 0.34931 | 0.93125 | 0.69514 | 0.83333 | 0.20833 | 0.68125 | 0.74653 | 0.76111 | 0.9 | 0.35556 | 0.58542 | 0.47431 | 0.42083 | 0.36042 | 0.42639 | 0.71042 | 0.46875 | 0.44514 | 0.37778 | 0.55764 | 0.42639 | 0.52778 | 0.62222
KANO INDUSTRIAL | 15MVA TR1 DAN AGUNDI | ZOO ROAD | 11KV AJASA | A | 0.83333 | 20 | 3.3 | 1900-01-28 05:55 | 12845 | 1900-01-24 | 1900-01-16 12:38 | 0 | 0.5625 | 0.34444 | 0.69583 | 0.38611 | 0.58333 | 0.72222 | 0.42778 | 0.34931 | 0.93125 | 0.69514 | 0.66667 | 0.55556 | 0.89931 | 0.42222 | 0.63958 | 0.825 | 0.46806 | 0.81806 | 0.44861 | 0.42083 | 0.66389 | 0.42639 | 0.78194 | 0.49722 | 0.64167 | 0.49028 | 0.60486 | 0.40694 | 0.48611 | 0.66528
KANO NORTH | 15MVA TR1 DAN AGUNDI | KANO CITY | 11KV IBRAHIM TAIWO | C | 0.5 | 12 | 4.7 | 1900-01-28 01:20 | 15600 | 1900-01-14 | 1900-01-16 09:18 | 0.79167 | 0.5625 | 0.34444 | 0.75 | 0.34861 | 0.44653 | 0.74931 | 0.42778 | 0.29861 | 0.75 | 0.69514 | 0.66667 | 0.079861 | 0.89931 | 0.49653 | 0.42778 | 0.82847 | 0.46806 | 0.78056 | 0.50972 | 0.42083 | 0.51111 | 0.42639 | 0.78194 | 0.49931 | 0.60625 | 0.49028 | 0.56597 | 0.47986 | 0.45139 | 0.83264
KANO NORTH | 15MVA TR2 DAN AGUNDI | KANO CITY | 11KV CITY | C | 0.5 | 12 | 4.3 | 1900-01-28 19:28 | 11900 | 1900-01-14 | 1900-01-15 15:05 | 0.53333 | 0.54167 | 0.40069 | 0.29167 | 0.22986 | 0.34792 | 0.11736 | 0.64306 | 0.325 | 0.75 | 0.65 | 0.55972 | 0.51806 | 0.92639 | 0.65278 | 0.86181 | 0.89583 | 0.32708 | 0.60764 | 0.43194 | 0.39931 | 0.44236 | 0.44792 | 0.69931 | 0.56736 | 0.40694 | 0.62708 | 0.86389 | 0.2625 | 0.65139 | 0.64861
KANO NORTH | 15MVA TR2 DAN AGUNDI | KANO CITY | 11KV KOFAR NAISA | C | 0.5 | 12 | 4.3 | 1900-01-29 | 12200 | 1900-01-14 | 1900-01-12 04:35 | 0.25 | 0.47292 | 0.10625 | 0.35417 | 0.15 | 0.45833 | 0.10764 | 0.40417 | 0.325 | 0.57083 | 0.65 | 0.675 | 0 | 0.30069 | 0.56875 | 0.76111 | 0.62361 | 0.13056 | 0.60764 | 0.43194 | 0.39931 | 0.35903 | 0.44792 | 0.69931 | 0.71528 | 0.40694 | 0.50625 | 0.13333 | 0.34792 | 0.65139 | 0.57569
KANO NORTH | 15MVA TR1 GORON DUTSE | KANO CITY | 11KV JAKARA | D | 0.33333 | 8 | 4.2 | 1900-01-28 08:13 | 10450 | 1900-01-09 | 1900-01-04 15:34 | 0.11389 | 0.056944 | 0.25694 | 0.091667 | 0.10764 | 0.16667 | 0.041667 | 0.14861 | 0.20833 | 0.25 | 0.40208 | 0.20833 | 0 | 0.1 | 0.11597 | 0.22361 | 0.19236 | 0.086806 | 0.2625 | 0.18056 | 0.32986 | 0.15833 | 0 | 0.26319 | 0.22778 | 0.17569 | 0.24236 | 0.12292 | 0.26042 | 0.26111 | 0.39236
KANO NORTH | 15MVA TR1 GORON DUTSE | RIJIYAR ZAKI | 11KV AMINU KANO | C | 0.5 | 12 | 3.5 | 1900-01-26 21:42 | 6700 | 1900-01-14 | 1900-01-06 05:27 | 0.375 | 0.0625 | 0.31111 | 0.091667 | 0.014583 | 0.125 | 0.083333 | 0.092361 | 0.22708 | 0.19792 | 0.41667 | 0.38681 | 0.16667 | 0.41319 | 0.2875 | 0.28611 | 0.325 | 0.048611 | 0.43819 | 0.16319 | 0.39306 | 0.26528 | 0.018056 | 0.30833 | 0.33403 | 0.079167 | 0.13958 | 0.073611 | 0.30694 | 0.30903 | 0.4875
KANO NORTH | 15MVA TR2 GORON DUTSE | RIJIYAR ZAKI | 11KV SANI MAINAGGE | C | 0.5 | 12 | 5.3 | 1900-01-27 18:01 | 8000 | 1900-01-14 | 1900-01-05 23:36 | 0.22917 | 0.064583 | 0.33333 | 0.091667 | 0.19792 | 0.17569 | 0.065278 | 0.16667 | 0.22708 | 0.18125 | 0.375 | 0.30903 | 0.041667 | 1899-12-31 | 0.061111 | 0.22361 | 0.28819 | 0.094444 | 0.3125 | 0.20486 | 0.22569 | 0.13472 | 0.018056 | 0.29653 | 0.29583 | 0.084722 | 0.29653 | 0.31181 | 0.21528 | 0.19097 | 0.27014
KANO NORTH | 15MVA TR2 GORON DUTSE | RIJIYAR ZAKI | 11KV KABUGA | B | 0.66667 | 16 | 7.3 | 2022-09-04 15:55 | 18700 | 1900-01-19 | 1900-01-06 00:41 | 0.27917 | 0.083333 | 0.27431 | 0.041667 | 0.075 | 0.15556 | 0.018056 | 0.20833 | 0.25764 | 0.47708 | 0.35347 | 0.40208 | 0.125 | 0.48611 | 0.18542 | 0.29861 | 0.26181 | 0.083333 | 0.37778 | 0.088194 | 0.30278 | 0.10417 | 0 | 0.35833 | 0.24028 | 0.3125 | 0.072222 | 0.073611 | 0.40972 | 0.29653 | 0.32639
KANO NORTH | 7.5MVA TR1 NIPP RADIO HOUSE | KANO CITY | 11KV BELLO DANDAGO | A | 0.83333 | 20 | 0.1 | 1900-01-28 19:42 | 700 | 1900-01-24 | 1900-01-14 01:21 | 0.56458 | 0.375 | 0.85486 | 0.39514 | 0.54167 | 0.51319 | 0.065278 | 0.30208 | 0.31111 | 0.38542 | 0.75 | 0.63958 | 0.096528 | 0.33819 | 0.21875 | 0.46944 | 0.36111 | 0.33542 | 0.66181 | 0.22569 | 0.84097 | 0.7375 | 0.35139 | 0.71389 | 0.44653 | 0.80278 | 0.12639 | 0.66042 | 0.48333 | 0.48889 | 0.99931
KANO NORTH | 15MVA TR1 ADO BAYERO | KANO CITY | 11KV SAGAGI | D | 0.33333 | 8 | 1.2 | 1900-01-27 22:30 | 4100 | 1900-01-09 | 1900-01-11 13:34 | 0.42847 | 0.375 | 0.64653 | 0.39097 | 0.18056 | 0.16667 | 0.15903 | 0.29167 | 0.30833 | 0.375 | 0.44931 | 0.63889 | 0.094444 | 0.33403 | 0.20278 | 0.46389 | 0.61875 | 0.18958 | 0.65139 | 0.22292 | 0.20694 | 0.63264 | 0.34375 | 0.70417 | 0.44236 | 0.23681 | 0.11528 | 0.65972 | 0.48333 | 0.56944 | 0.98264
KANO NORTH | 15MVA TR1 BUKAVU | RIJIYAR ZAKI | 11KV BACHIRAWA | C | 0.5 | 12 | 5.8 | 2022-09-08 20:44 | 19300 | 1900-01-14 | 1900-01-05 01:24 | 0.14028 | 0.125 | 0.25 | 0.25 | 0.054167 | 0.33333 | 0.027778 | 0.0097222 | 0 | 0.083333 | 0.36389 | 0.27222 | 0 | 0.014583 | 0 | 0.079861 | 0.34028 | 0.28472 | 0.24167 | 0.072917 | 0.60347 | 0.26389 | 0.31389 | 0.42083 | 0.25347 | 0.42778 | 0.10833 | 0.14236 | 0.13472 | 0.21667 | 0.22917
KANO CENTRAL | 15MVA TR1 BUKAVU | SABON GARI | 11KV NOMANSLAND | B | 0.66667 | 16 | 2 | 1900-01-29 | 12550 | 1900-01-19 | 1900-01-07 22:59 | 0.16667 | 0 | 0.375 | 0.375 | 0.39931 | 0.33333 | 0.041667 | 0.26875 | 0.14375 | 0.26111 | 0.5 | 0.48194 | 0 | 0.20139 | 0.095833 | 0.16181 | 0.47847 | 0.28472 | 0.40278 | 0.21181 | 0.68819 | 0.20417 | 0.34306 | 0.46458 | 0.45278 | 0.47847 | 0.097917 | 0.21528 | 0.10764 | 0.34028 | 0.38194
KANO NORTH | 15MVA TR2 BUKAVU | IDH | 11KV FEDERAL SECRETARIAT | C | 0.5 | 12 | 4.7 | 1900-01-28 09:00 | 15800 | 1900-01-14 | 1900-01-05 15:23 | 0.14028 | 0 | 0.070139 | 0.070139 | 0.13333 | 0.33333 | 0.024306 | 0.041667 | 0 | 0.0041667 | 0.54167 | 0.48542 | 0 | 0.20972 | 0.10208 | 0.30139 | 0.4375 | 0.28472 | 0.35208 | 0.20833 | 0.30139 | 0.16319 | 0.33681 | 0.42708 | 0.38542 | 0.46944 | 0.025 | 0.0034722 | 0.21389 | 0.26597 | 0.30903
KANO NORTH | 15MVA TR2 BUKAVU | IDH | 11KV ORTHOPAEDIC | C | 0.5 | 12 | 4 | 1900-01-28 00:45 | 13950 | 1900-01-14 | 1900-01-06 08:44 | 0.10903 | 0 | 0.375 | 0.375 | 0.11319 | 0.24097 | 0.065972 | 0.125 | 0 | 0.20833 | 0.51389 | 0.48125 | 0 | 0.10139 | 0 | 0.30139 | 0.32153 | 0.175 | 0.4375 | 0.21528 | 0.65069 | 0.1875 | 0.0069444 | 0.47014 | 0.38194 | 0.38681 | 0.049306 | 0.22917 | 0.19444 | 0.25139 | 0.39583
KANO CENTRAL | 15MVA TR2 BUKAVU | SABON GARI | 11KV FANISAU | D | 0.33333 | 8 | 5.3 | 1900-01-25 02:26 | 25450 | 1900-01-09 | 1900-01-05 00:42 | 0.125 | 0 | 0.375 | 0.375 | 0.0097222 | 0.33333 | 0.024306 | 0.0020833 | 0.22431 | 0.26111 | 0.26042 | 0.125 | 0 | 0 | 0 | 0.054167 | 0.63264 | 0.28264 | 0.33194 | 0.22569 | 0.60903 | 0.15139 | 0 | 0.045833 | 0.027083 | 0.65417 | 0.10833 | 0.19583 | 0.061806 | 0.077778 | 0.45556
KANO NORTH | 15MVA TR1 I.D.H. | IDH | 11KV FAGGE | C | 0.5 | 12 | 3 | 1900-01-28 22:15 | 15700 | 1900-01-14 | 1900-01-11 16:24 | 0.48264 | 0.15278 | 0.25 | 0.45833 | 0.30278 | 0.19722 | 0.44028 | 0.59861 | 0.39931 | 0.47917 | 0.44028 | 0.41667 | 0.20833 | 0.37014 | 0.56042 | 0.68958 | 0.72222 | 0.36806 | 0.45069 | 0.52153 | 0.26042 | 0.375 | 0.3875 | 0.65764 | 0.46181 | 0.29167 | 0.25 | 0.21181 | 0.33542 | 0.085417 | 0.85764
KANO NORTH | 15MVA TR2 I.D.H. | IDH | 11KV GWAMMAJA | D | 0.33333 | 8 | 2.7 | 1900-01-28 22:38 | 9000 | 1900-01-09 | 1900-01-08 00:32 | 0.39931 | 0 | 0.098611 | 0.34306 | 0.23403 | 0.125 | 0.375 | 0.55 | 0.41667 | 0.64097 | 0.44028 | 0.41667 | 0.20833 | 0.25903 | 0.51806 | 0 | 0 | 0 | 0 | 0 | 0.083333 | 0.375 | 0.3875 | 0.65764 | 0.46181 | 0.29167 | 0.25 | 0.21181 | 0.33542 | 0.085417 | 0.85764
KANO CENTRAL | 15MVA TR2 I.D.H. | SABON GARI | 11KV SABON GARI | B | 0.66667 | 16 | 4 | 1900-01-28 16:50 | 12800 | 1900-01-19 | 1900-01-12 17:00 | 0.58333 | 0.26458 | 0.33333 | 0.2625 | 0.31181 | 0.16667 | 0.44028 | 0.59861 | 0.31181 | 0.85833 | 0.41667 | 0.43333 | 0.22569 | 0.33333 | 0.59028 | 0.67708 | 0.63194 | 0.29167 | 0.71597 | 0.46389 | 0.58333 | 0.41667 | 0.37569 | 0.52569 | 0.45556 | 0.31736 | 0.26042 | 0.28472 | 0.47431 | 0.44583 | 0.65764
KANO CENTRAL | 15MVA TR3 I.D.H. | SABON GARI | 11KV ABUJA ROAD | B | 0.66667 | 16 | 2.5 | 1900-01-29 | 9250 | 1900-01-19 | 1900-01-12 17:08 | 0.58333 | 0.26458 | 0.27708 | 0.25 | 0.25 | 0.27153 | 0.44028 | 0.59167 | 0.25 | 0.92708 | 0.5 | 0.43333 | 0.20833 | 0.37639 | 0.37569 | 0.60486 | 0.71875 | 0.375 | 0.72639 | 0.54722 | 0.60694 | 0.44444 | 0.3625 | 0.66806 | 0.41875 | 0.33056 | 0.14097 | 0.18403 | 0.42917 | 0.45417 | 0.70278
KANO NORTH | 15MVA TR3 I.D.H. | IDH | 11KV KOKI | D | 0.33333 | 8 | 2.2 | 1900-01-29 20:45 | 10400 | 1900-01-09 | 1900-01-11 07:03 | 0.42431 | 0.15347 | 0.25 | 0.39861 | 0.29167 | 0.16667 | 0.375 | 0.49583 | 0.45833 | 0.78264 | 0.47917 | 0.43333 | 0.20833 | 0.29931 | 0.54167 | 0.66389 | 0.65694 | 0.10903 | 0.70069 | 0.47778 | 0.44583 | 0.275 | 0.35278 | 0.46875 | 0.28819 | 0.26111 | 0.32778 | 0.27361 | 0.42708 | 0.34722 | 0.45972
KANO CENTRAL | 15MVA TR1 SMALL SCALE | BOMPAI | 11KV TUDUN MURTALA | D | 0.33333 | 8 | 0.7 | 2022-09-10 05:48 | 4050 | 1900-01-09 | 1900-01-11 16:15 | 0.55417 | 0.45069 | 0.20833 | 0.29167 | 0.19722 | 0.29167 | 0.17708 | 0.083333 | 0.45833 | 0.53403 | 0.51528 | 0.33333 | 0.59375 | 0.37431 | 0.41181 | 0.59931 | 0.83958 | 0.54167 | 0.29722 | 0.13403 | 0.38542 | 0.40208 | 0.26389 | 0.48264 | 0.38194 | 0.25 | 0.21111 | 0.61319 | 0.36667 | 0.7125 | 0.72083
KANO CENTRAL | 15MVA TR1 SMALL SCALE | BOMPAI | 11KV RIMIN KEBE | D | 0.33333 | 8 | 5.2 | 1900-01-28 21:48 | 10950 | 1900-01-09 | 1900-01-12 00:34 | 0.55417 | 0.45069 | 0.20833 | 0.68611 | 0.23681 | 0.31458 | 0.43819 | 0.083333 | 0.45833 | 0.43542 | 0.51528 | 0.33333 | 0.55208 | 0.37431 | 0.41111 | 0.52361 | 0.65 | 0.54167 | 0.29722 | 0.13403 | 0.37431 | 0.47431 | 0.26389 | 0.47986 | 0.38194 | 0.25 | 0.20764 | 0.61319 | 0.32778 | 0.70833 | 0.74375
KANO INDUSTRIAL | 15MVA TR1 SHARADA | SHARADA | 11KV HOUSING ESTATE | B | 0.66667 | 16 | 4 | 2022-09-10 05:17 | 8550 | 1900-01-19 | 1900-01-15 21:03 | 0.051389 | 0.64722 | 0.39653 | 0.5 | 0.46528 | 0.33333 | 0.73542 | 0.34097 | 0.84028 | 0.80903 | 0.69653 | 0.45833 | 0.56944 | 0.40139 | 0.55972 | 0.69861 | 1899-12-31 | 0.79167 | 0.46458 | 0.42292 | 0.26806 | 0.57569 | 0.49097 | 0.72292 | 0.50556 | 0.4 | 0.23333 | 0.525 | 0.55903 | 0.86042 | 0.55347
KANO INDUSTRIAL | 15MVA TR1 SHARADA | SHARADA | 11KV NNDC | B | 0.66667 | 16 | 4.3 | 1900-01-29 | 9350 | 1900-01-19 | 1900-01-12 21:51 | 0.41667 | 0.61181 | 0.36389 | 0.17639 | 0.46667 | 0.31181 | 0.56319 | 0.47292 | 0.84028 | 0.70833 | 0.66667 | 0.45833 | 0.25694 | 0.35139 | 0.37361 | 0.44028 | 0.91667 | 0.75 | 0.24375 | 0.25486 | 0.38125 | 0.42708 | 0.38194 | 0.70347 | 0.36181 | 0.34583 | 0.20764 | 0.18264 | 0.31319 | 0.54653 | 0.41458
KANO INDUSTRIAL | 15MVA TR2 SHARADA | ZOO ROAD | 11KV TUKUNTAWA | C | 0.5 | 12 | 4.7 | 1900-01-28 18:59 | 8775 | 1900-01-14 | 1900-01-10 09:01 | 0 | 0.28611 | 0.25 | 0.10069 | 0.38889 | 0.20417 | 0.54861 | 0.22917 | 0.29861 | 0.75694 | 0.55 | 0.5 | 0.20833 | 0.35 | 0.42153 | 0.58889 | 0.5 | 0.68125 | 0.39167 | 0.35278 | 0.35972 | 0.18542 | 0.36944 | 0.46458 | 0.48681 | 0.25347 | 0.16806 | 0.31944 | 0.36389 | 0.38819 | 0.40903
KANO INDUSTRIAL | 15MVA TR2 SHARADA | ZOO ROAD | 11KV SHARADA INDUSTRIAL | A | 0.83333 | 20 | 4.3 | 1900-01-28 09:00 | 9950 | 1900-01-24 | 1900-01-13 09:11 | 0.625 | 0.66111 | 0.375 | 0.40625 | 0.42361 | 0.28819 | 0.73264 | 0.43125 | 0.29861 | 0.84028 | 0.63333 | 0.54167 | 0.66667 | 0.22778 | 0.40139 | 0.55208 | 0.92361 | 0.66667 | 0.3875 | 0.37847 | 0.14722 | 0.30069 | 0.37431 | 0.65 | 0.37778 | 0.29306 | 0.20139 | 0.16458 | 0.27639 | 0.73194 | 0.40417
KANO INDUSTRIAL | 15MVA TR1 GONGONI | DORAYI | 11KV JAEN | D | 0.33333 | 8 | 5 | 1900-01-27 23:46 | 12425 | 1900-01-09 | 1900-01-09 15:32 | 0.125 | 0.20833 | 0.34375 | 0.17569 | 0.25 | 0.15278 | 0.20833 | 0.20833 | 0.32083 | 0.51528 | 0.67986 | 0.47847 | 0.47292 | 0.22986 | 0.27431 | 0.36806 | 0.51597 | 0.66667 | 0.36806 | 0.27986 | 0.29514 | 0.35764 | 0.35208 | 0.46806 | 0.32986 | 0.22222 | 0.21806 | 0.083333 | 0.25 | 0.51875 | 0.70972
KANO INDUSTRIAL | 15MVA TR1 GONGONI | DORAYI | 11KV CHIRANCI | D | 0.33333 | 8 | 5.3 | 2022-09-07 02:33 | 9700 | 1900-01-09 | 1900-01-10 20:55 | 0.33333 | 0.31042 | 0.29167 | 0.21736 | 0.29167 | 0.20833 | 0.39722 | 0.39722 | 0.38472 | 0.59375 | 0.625 | 0.43819 | 0.47292 | 0.32986 | 0.31806 | 0.19444 | 0.82986 | 0.73681 | 0.34792 | 0.25625 | 0.34653 | 0.35278 | 0.29861 | 0.50694 | 0.29444 | 0.29861 | 0.14861 | 0.15208 | 0.24444 | 0.54375 | 0.70972
KANO INDUSTRIAL | 15MVA TR1 GONGONI | SHARADA | 11KV MUNDADU | D | 0.33333 | 8 |  | 1900-01-28 07:28 |  | 1900-01-09 | 1900-01-14 20:23 | 0.42986 | 0.41667 | 0.39583 | 0.75 | 0.58333 | 0.25 | 0.80764 | 0.80764 | 0.36528 | 0.7375 | 0.66667 | 0.60556 | 0.62083 | 0.24861 | 0.42708 | 0.60972 | 0.80347 | 0.76944 | 0.23611 | 0.26181 | 0.36181 | 0.53542 | 0.5 | 0.63194 | 0.425 | 0.32014 | 0.41667 | 0.47222 | 0.33125 | 0.52014 | 0.54167
KANO INDUSTRIAL | 7.5MVA TR2 GONGONI | SHARADA | 11KV DALA FOODS | A | 0.83333 | 20 | 2.3 | 1900-01-28 15:10 | 9650 | 1900-01-24 | 1900-01-24 05:36 | 0.56736 | 0.81875 | 0.8125 | 0.74583 | 1899-12-31 | 0.77639 | 0.82361 | 0.82361 | 0.8875 | 0.88403 | 0.875 | 0.77639 | 0.89653 | 0.66667 | 0.90069 | 0.95347 | 1899-12-31 | 0.77083 | 0.71667 | 0.525 | 0.94097 | 0.72778 | 0.60208 | 0.85 | 0.81111 | 0.97222 | 0.59583 | 0.53333 | 0.97917 | 1899-12-31 | 1899-12-31
KANO INDUSTRIAL | 15MVA TR1 ZARIA ROAD | AKTH | 11KV KARKASARA | C | 0.5 | 12 | 5.6 | #VALUE! | 12800 | 1900-01-14 | 1900-01-12 15:40 | 0.22639 | 0.19236 | 0.23264 | 0.21875 | 0.27292 | 0.27778 | 0.43819 | 0.27778 | 0.43819 | 0.53264 | 0.33333 | 0.41667 | 0.63611 | 0.63056 | 0.51389 | 0.71944 | 0.42569 | 0.39236 | 0.61181 | 0.43403 | 0.62708 | 0.51528 | 0.49861 | 0.54167 | 0.44375 | 0.25486 | 0.32917 | 0.59583 | 0.48333 | 0.51667 | 0.625
KANO EAST | 15MVA TR1 ZARIA ROAD | HOTORO | 11KV KUNDILA | C | 0.5 | 12 | 3 | 1900-01-28 06:21 | 10350 | 1900-01-14 | 1900-01-10 21:29 | 0.36111 | 0.15069 | 0.20833 | 0.15417 | 0.19653 | 0.25 | 0.26111 | 0.20833 | 0.26111 | 0.45069 | 0.41667 | 0.39167 | 0.56597 | 0.78889 | 0.18125 | 0.78125 | 0.43194 | 0.23611 | 0.70278 | 0.37986 | 0.58889 | 0.49028 | 0.42569 | 0.63889 | 0.35208 | 0.25903 | 0.17986 | 0.50556 | 0.37708 | 0.26181 | 0.4375
KANO INDUSTRIAL | 15MVA TR3 ZARIA ROAD | AKTH | 11KV SALLARI | C | 0.5 | 12 | 4.8 | 1900-01-28 21:40 | 8900 | 1900-01-14 | 1900-01-11 18:42 | 0.32292 | 0.14583 | 0.14375 | 0.23333 | 0.25 | 0.26528 | 0.375 | 0.26528 | 0.375 | 0.40694 | 0.29167 | 0.41319 | 0.5 | 0.76389 | 0.57292 | 0.63056 | 0.48125 | 0.40556 | 0.73472 | 0.31528 | 0.62778 | 0.34028 | 0.42569 | 0.61667 | 0.34444 | 0.2125 | 0.18194 | 0.60903 | 0.47222 | 0.30556 | 0.75069
KANO EAST | 15MVA TR2 ZARIA ROAD | HOTORO | 11KV UNGUWA UKU | C | 0.5 | 12 | 5.8 | 1900-01-29 | 12650 | 1900-01-14 | 1900-01-10 13:23 | 0.36597 | 0.053472 | 0.21806 | 0.23333 | 0.16667 | 0.32153 | 0.375 | 0.32153 | 0.375 | 0.46875 | 0.083333 | 0.30764 | 0.625 | 0.65139 | 0.56806 | 0.72917 | 0.36806 | 0.16667 | 0.13681 | 0.24514 | 0.5 | 0.24306 | 0.59306 | 0.57778 | 0.42153 | 0.31111 | 0.12708 | 0.59861 | 0.38889 | 0.38819 | 0.62778
KANO EAST | 15MVA TR2 ZARIA ROAD | HOTORO | 11KV HOTORO | C | 0.5 | 12 | 3.7 | 1900-01-27 21:22 | 9250 | 1900-01-14 | 1900-01-11 16:30 | 0.20833 | 0.053472 | 0.20833 | 0 | 0.36736 | 0.22986 | 0.32222 | 0.22986 | 0.32222 | 0.5 | 0.46597 | 0.059028 | 0.65486 | 0.58681 | 0.66667 | 0.54167 | 0.60278 | 0.32431 | 0.85208 | 0.36111 | 0.59375 | 0.37222 | 0.43125 | 0.67014 | 0.42917 | 0.32222 | 0.2125 | 0.45069 | 0.42986 | 0.52917 | 0.68958
KANO INDUSTRIAL | 15MVA TR3 ZARIA ROAD | AKTH | 11KV HAUSAWA | C | 0.5 | 12 | 2.7 | 1900-01-28 21:40 | 7250 | 1900-01-14 | 1900-01-14 03:31 | 0.26389 | 0.16667 | 0.23264 | 0.3625 | 0.24097 | 0.40903 | 0.2375 | 0.40903 | 0.2375 | 0.60208 | 0.39236 | 0.47431 | 0.8 | 0.79306 | 0.63403 | 0.64444 | 0.56944 | 0.475 | 0.93958 | 0.55903 | 0.58681 | 0.55556 | 0.56806 | 0.75347 | 0.38333 | 0.31042 | 0.18125 | 0.54236 | 0.54028 | 0.63611 | 0.64583
KANO INDUSTRIAL | 15MVA TR3 ZARIA ROAD | AKTH | 11KV MARHABA | C | 0.5 | 12 | 4.9 | 1900-01-28 23:29 | 10425 | 1900-01-14 | 1900-01-13 02:44 | 0.34861 | 0.1 | 0.20833 | 0.25 | 0.22292 | 0.29167 | 0.41667 | 0.29167 | 0.41667 | 0.45833 | 0.40625 | 0.36736 | 0.70833 | 0.74861 | 0.72222 | 0.5875 | 0.5375 | 0.30972 | 0.83958 | 0.40486 | 0.72917 | 0.6125 | 0.40694 | 0.61042 | 0.42083 | 0.32569 | 0.18125 | 0.57917 | 0.37014 | 0.53333 | 0.70764
KANO INDUSTRIAL | 15MVA TR1 ABATTOIR | DORAYI | 11KV CERAMIC | A | 0.83333 | 20 | 1.3 | 1900-01-29 | 6100 | 1900-01-24 | 1900-01-26 17:09 | 0.94028 | 1899-12-31 | 0.51736 | 0.97569 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.98056 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.45069 | 0.95833 | 0.98681 | 0.60903 | 0.96319 | 0.98125 | 0.62569 | 0.39722 | 0.95278 | 0.99514 | 0.72778 | 0.88056 | 1899-12-31 | 0.77222 | 1899-12-31
KANO INDUSTRIAL | 15MVA TR1 ABATTOIR | DORAYI | 11KV NBC | A | 0.83333 | 20 | 4.4 | 1900-01-29 | 13450 | 1900-01-24 | 1900-01-26 07:12 | 0.875 | 1899-12-31 | 0.51042 | 0.97569 | 1899-12-31 | 1899-12-31 | 0.98958 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.45069 | 0.95833 | 0.98125 | 0.31875 | 0.96319 | 0.93819 | 0.62569 | 0.39722 | 0.95278 | 0.99514 | 0.72778 | 0.88056 | 1899-12-31 | 0.77222 | 0.9875
KANO WEST | 15MVA TR1 ABATTOIR | PANSHEKARA | 11KV ZAWACIKI | C | 0.5 | 12 | 3.7 | 1900-01-28 20:14 | 7950 | 1900-01-14 | 1900-01-16 03:35 | 0.40556 | 0.86667 | 0.51042 | 0.475 | 0.47917 | 0.625 | 0.47778 | 0.4375 | 0.75 | 1899-12-31 | 0.91667 | 1899-12-31 | 0.60417 | 0.48056 | 0.41319 | 0.41389 | 0.35556 | 0.52083 | 0.61319 | 0.60903 | 0.5125 | 0.48333 | 0.48472 | 0.33542 | 0.51875 | 0.53542 | 0.3125 | 0.45208 | 0.47014 | 0.40833 | 0.68194
KANO WEST | 7.5MVA TR1 CHALLAWA | PANSHEKARA | 11KV CHALAWA WATER PLANT |  | 0.83333 | 20 | 2.7 | 1900-01-29 | 5500 | 1900-01-24 | 1900-01-26 10:01 | 0.92569 | 0.77986 | 1899-12-31 | 0.5 | 1899-12-31 | 1899-12-31 | 0.56528 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.9875 | 0.875 | 1899-12-31 | 0.95972 | 0.85278 | 1899-12-31 | 0.84653 | 0.875 | 0.92083 | 0.54306 | 0.93611 | 0.57569 | 0.58472 | 1899-12-31 | 0.91944 | 0.9875 | 0.98958 | 1899-12-31 | 0.89653 | 0.89653 | 1899-12-31
KANO WEST | 7.5MVA TR2 CHALLAWA | PANSHEKARA | 11KV PANSHEKARA | C | 0.5 | 12 | 2.9 | 1900-01-28 21:18 | 5800 | 1900-01-14 | 1900-01-22 07:15 | 0.625 | 0.5 | 1899-12-31 | 0.27917 | 0.52639 | 0.66667 | 0.30903 | 0.73403 | 1899-12-31 | 1899-12-31 | 0.9875 | 0.875 | 0.91667 | 0.49097 | 0.77292 | 0.99306 | 0.84653 | 0.49028 | 0.89931 | 0.54167 | 0.93611 | 0.57569 | 0.58472 | 0.90556 | 0.78958 | 0.76319 | 0.72083 | 0.88889 | 0.84167 | 0.84167 | 1899-12-31
KANO WEST | 15MVA TR1 TAMBURAWA | MAIKALWA | 11KV TAMBURAWA WATER PLANT | A | 0.83333 | 20 | 3 | 1900-01-29 | 7000 | 1900-01-24 | 1900-01-22 00:29 | 0.49167 | 0.64583 | 0.79931 | 0.85417 | 0.63194 | 0.98958 | 0.98958 | 0.94444 | 0.875 | 0.86389 | 0.93889 | 0.85417 | 0.99028 | 0.94097 | 0.85069 | 1899-12-31 | 0.6875 | 0.22222 | 0.89583 | 0.51389 | 0.95833 | 0.28056 | 0.21528 | 0.92222 | 0.63889 | 0.77708 | 0.72986 | 0.35417 | 0.94861 | 0.84028 | 0.375
KANO WEST | 7.5MVA TR1 NA'IBAWA | MAIKALWA | 11KV YANLEMO | C | 0.5 | 12 | 2.4 | 1900-01-28 04:02 | 11000 | 1900-01-14 | 1900-01-14 12:21 | 0.52083 | 0.25972 | 0.29167 | 0.39583 | 0.33333 | 0.25 | 0.41667 | 0.375 | 0.375 | 0.45833 | 0.64653 | 0.74028 | 0.90694 | 0.58542 | 0.37153 | 0.6875 | 0.75347 | 0.33472 | 0.84375 | 0.54514 | 0.66389 | 0.25625 | 0.11597 | 0.89375 | 0.34722 | 0.60764 | 0.29931 | 0.22569 | 0.69653 | 0.50764 | 0.80903
KANO WEST | 7.5MVA TR1 NA'IBAWA | MAIKALWA | 11KV MASARAUTA | B | 0.66667 | 16 | 1.5 | 1900-01-29 | 5000 | 1900-01-19 | 1900-01-15 22:53 | 0.59722 | 0.23958 | 0.33333 | 0.39583 | 0.36458 | 0.38472 | 0.13472 | 0.53056 | 0.35833 | 0.5625 | 0.575 | 0.86528 | 0.90694 | 0.62708 | 0.37361 | 0.76389 | 0.75347 | 0.45417 | 0.84028 | 0.42986 | 0.69931 | 0.37778 | 0.51597 | 0.89375 | 0.42014 | 0.63542 | 0.41736 | 0.27083 | 0.66181 | 0.67431 | 0.89583
KANO WEST | 7.5MVA TR1 NIPP LAW SCHOOL | KWANAR DANGORA | 11KV CAMPUS | C | 0.5 | 12 | 0.2 | 1900-01-29 | 2550 | 1900-01-14 | 1900-01-05 23:13 | 0.19236 | 0.325 | 0.20486 | 0.31458 | 0.49167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0.25278 | 0.22083 | 0.16736 | 0 | 0.55972 | 0.27639 | 0.19861 | 0.70833 | 0.20833 | 0.30417 | 0.27292 | 0.35903 | 0.30556 | 0.34028 | 0.81458
KANO WEST | 7.5MVA TR1 NIPP LAW SCHOOL | KWANAR DANGORA | 11KV TIGA | E | 0.16667 | 4 | 1.6 | 1900-01-29 | 4250 | 1900-01-04 | 1900-01-04 12:06 | 0.1125 | 0.325 | 0.20486 | 0.31458 | 0.49167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0.25278 | 0.22083 | 0.16736 | 0 | 0.4125 | 0.24167 | 0.10069 | 0.25 | 0.20833 | 0.30417 | 0.27292 | 0.33194 | 0.30556 | 0.1875 | 0.34931
KANO CENTRAL | 15MVA TR1 CLUB | KEDCO HQ | 11KV AHMADU BELLO | A | 0.83333 | 20 | 4.5 | 1900-01-27 17:59 | 24375 | 1900-01-24 | 1900-01-20 00:52 | 0.73611 | 0.61806 | 0.48264 | 0.70069 | 0.53472 | 0.54167 | 0.48611 | 0.64931 | 0.7625 | 0.93125 | 1899-12-31 | 0.63958 | 0.52083 | 0.8125 | 0.85556 | 0.72917 | 0.65278 | 0.36597 | 0.96528 | 0.45278 | 0.64375 | 0.85417 | 0.57639 | 0.47014 | 0.75764 | 0.59722 | 0.52222 | 0.84167 | 0.78472 | 0.68958 | 0.86111
KANO CENTRAL | 15MVA TR1 CLUB | BADAWA | 11KV RACE COURSE | B | 0.66667 | 16 | 2.7 | 2022-09-09 18:10 | 13050 | 1900-01-19 | 1900-01-18 08:31 | 0.65972 | 0.5 | 0.54167 | 0.70833 | 0.52083 | 0.61528 | 0.375 | 0.375 | 0.69097 | 0.93125 | 0.77778 | 0.72986 | 0.42569 | 0.80972 | 0.74028 | 0.72222 | 0.65139 | 0.52917 | 0.76389 | 0.28472 | 0.70556 | 0.96181 | 0.47847 | 0.65764 | 0.52083 | 0.51736 | 0.55625 | 0.76458 | 0.45486 | 0.59653 | 0.78819
KANO CENTRAL | 15MVA TR1 CLUB | BADAWA | 11KV BADAWA | B | 0.66667 | 16 | 3.7 | 1900-01-28 05:30 | 9150 | 1900-01-19 | 1900-01-20 06:39 | 0.73264 | 0.72778 | 0.43194 | 0.60278 | 0.58333 | 0.73819 | 0.4375 | 0.67917 | 0.76458 | 0.93125 | 0.95139 | 0.625 | 0.63889 | 0.82639 | 0.87778 | 0.96528 | 0.82778 | 0.50347 | 0.85417 | 0.40972 | 0.71389 | 0.84722 | 0.51736 | 0.55903 | 0.56944 | 0.44444 | 0.50903 | 0.60278 | 0.77778 | 0.72708 | 0.9
KANO CENTRAL | 15MVA TR2 CLUB | KEDCO HQ | 11KV BANK ROAD | A | 0.83333 | 20 | 4.3 | -30.7319 | 18350 | 1900-01-24 | 1900-01-19 07:52 | 0.72361 | 0.375 | 0.47708 | 0.72222 | 0.80556 | 0.38472 | 0.55694 | 0.80208 | 0.91667 | 0.96806 | 0.73472 | 0.75 | 1899-12-31 | 0.32639 | 0.76181 | 0.93056 | 0.90417 | 0.40208 | 0.88056 | 0.60417 | 0.50208 | 0.64583 | 0.47917 | 0.46806 | 0.4875 | 0.73472 | 0.26181 | 0.49236 | 0.60278 | 0.73819 | 0.88889
KANO CENTRAL | 15MVA TR2 CLUB | KEDCO HQ | 11KV AUDU BAKO | A | 0.83333 | 20 | 4.5 | 1900-01-28 18:04 | 18025 | 1900-01-24 | 1900-01-22 05:20 | 0.68264 | 0.69097 | 0.66667 | 0.72222 | 0.80556 | 0.58333 | 0.55694 | 0.77083 | 0.82431 | 0.96806 | 1899-12-31 | 0.54167 | 0.43056 | 0.8125 | 0.86944 | 0.80556 | 0.89444 | 0.59444 | 0.96181 | 0.60417 | 0.69931 | 0.96181 | 0.58056 | 0.75347 | 0.75347 | 0.64583 | 0.61944 | 0.9625 | 0.76389 | 0.84444 | 0.85139
KANO CENTRAL | 15MVA TR3 CLUB | SABON GARI | 11KV MURTALA MUHAMMED | B | 0.66667 | 16 | 3.7 | 1900-01-29 | 10950 | 1900-01-19 | 1900-01-13 01:15 | 0.74653 | 0.44444 | 0.20833 | 0.45069 | 0.54167 | 0.34792 | 0.47222 | 0.28472 | 0.41667 | 0.41667 | 0.72431 | 0.40417 | 0.22222 | 0.81111 | 0.46389 | 0.54028 | 0.53681 | 0.34514 | 0.83958 | 0.23611 | 0.72361 | 0.47917 | 0.20139 | 0.47708 | 0.43056 | 0.425 | 0.26806 | 0.27917 | 0.44444 | 0.55208 | 0.31806
KANO CENTRAL | 15MVA TR3 CLUB | BADAWA | 11KV LAMIDO | C | 0.5 | 12 | 3.7 | 1900-01-28 07:53 | 10474 | 1900-01-14 | 1900-01-12 06:44 | 0.20556 | 0.5 | 0.22708 | 0.3125 | 0.51389 | 0.22569 | 0.31389 | 0.21944 | 0.45833 | 0.96806 | 0.69097 | 0.5 | 0.30556 | 0.61111 | 0.53333 | 0.59722 | 0.6375 | 0.22222 | 0.61806 | 0.35417 | 0.39792 | 0.47917 | 0.40972 | 0.43889 | 0.35417 | 0.42708 | 0.31389 | 0.32014 | 0.43056 | 0.36944 | 0.325
KANO CENTRAL | 15MVA TR1 FARM CENTER | KEDCO HQ | 11KV DR BALA | A | 0.83333 | 20 | 0.9 | 1900-01-28 09:40 | 10440 | 1900-01-24 | 1900-01-22 11:33 | 0.83333 | 0.87083 | 0.91667 | 0.81319 | 0.66667 | 0.80694 | 0.48611 | 0.54167 | 0.44167 | 0.91667 | 0.875 | 0.76806 | 0.98194 | 0.75347 | 0.96597 | 0.80972 | 0.57153 | 0.083333 | 0.96458 | 0.65833 | 0.90625 | 0.86528 | 0.59583 | 0.77639 | 0.99097 | 0.49306 | 0.80764 | 0.98681 | 0.95903 | 0.72778 | 0.64653
KANO EAST | 15MVA TR2 FARM CENTER | HOTORO | 11KV TARAUNI | A | 0.83333 | 20 | 0.4 | 2022-09-10 01:28 | 17900 | 1900-01-24 | 1900-01-17 21:58 | 0.39931 | 0.70833 | 0.91667 | 0.375 | 0.64583 | 0.68056 | 0.25903 | 0.89722 | 0.41667 | 0.91667 | 0.875 | 0.52222 | 0.68472 | 0.21181 | 0.36597 | 0.225 | 0.55139 | 0.031944 | 0.52917 | 0.65139 | 0.90625 | 0.85417 | 0.59583 | 0.88264 | 0.99097 | 0.38958 | 0.72292 | 0.35833 | 0.74306 | 0.90417 | 0.70347
KANO EAST | 7.5MVA TR2 MARIRI | HOTORO | 11KV DANLADI NASIDI | B | 0.66667 | 16 | 1.7 | 1900-01-28 18:30 | 3700 | 1900-01-19 | 1900-01-13 13:27 | 0.17847 | 1899-12-31 | 0.69861 | 0.19306 | 0.24167 | 0.35069 | 0.50903 | 0.60625 | 0.75 | 0.64722 | 0.34375 | 0.68056 | 0.45833 | 0.65347 | 0.76389 | 0.35 | 0.10208 | 0.26944 | 1899-12-31 | 0.10694 | 0.29028 | 0.14028 | 0.34 | 0.64236 | 0.44792 | 0.88681 | 0.75139 | 0.34653 | 0.13542 | 0.34236 | 0.33333
KANO EAST | 7.5MVA TR2 MARIRI | HOTORO | 11KV MAIDUGURI ROAD | C | 0.5 | 12 | 4 | 1900-01-26 06:45 | 8100 | 1900-01-14 | 1900-01-07 23:06 | 0.10694 | 0.56458 | 0.43681 | 0.068056 | 0 | 0.16667 | 0.43958 | 0.083333 | 0.30278 | 0.60694 | 0.66667 | 0.54167 | 0.031944 | 0.65069 | 0.57222 | 0.13194 | 0.085417 | 0.16667 | 0.56667 | 0.051389 | 0.25 | 0.0020833 | 0.34 | 0.14375 | 0.22083 | 0.61042 | 0.47014 | 0.14653 | 0.11806 | 0.14861 | 0.27083
KANO EAST | 7.5MVA TR1 MARIRI | HOTORO | 11KV FARAWA | C | 0.5 | 12 | 4 | -29.3229 | 10050 | 1900-01-14 | 1900-01-08 12:33 | 0.47569 | 0.47292 | 0.40694 | 0.125 | 0.041667 | 0.18056 | 0.52847 | 0.41667 | 0.51528 | 0.39861 | 0.29167 | 0.56597 | 0.11667 | 0.20694 | 0.39097 | 0.14097 | 0.061111 | 0.26944 | 0.83333 | 0.079167 | 0.10139 | 0.13889 | 0.34 | 0.46458 | 0.22639 | 0.58611 | 0.55208 | 0.13958 | 0.14236 | 0.089583 | 0.22361
KANO EAST | 15MVA TR1 JOGANA | KAWAJI | 11KV TALAMIZ | D | 0.33333 | 8 | 2.3 | 1900-01-25 11:46 | 11700 | 1900-01-09 | 1900-01-11 10:45 | 0.083333 | 0.29167 | 0.31389 | 0.33333 | 0.22292 | 0.16667 | 0.44097 | 0.54167 | 0.625 | 0.625 | 0.58333 | 0.45069 | 0.10069 | 0.59444 | 0.36667 | 0.65903 | 0.55833 | 0.17292 | 0.69931 | 0.35625 | 0.43264 | 0.49306 | 0.12014 | 0.72569 | 0.38056 | 0.28194 | 0.125 | 0.11875 | 0.60139 | 0.21667 | 0.76597
KANO EAST | 15MVA TR1 JOGANA | KAWAJI | 11KV TOKARAWA | A | 0.83333 | 20 | 0.7 | 1900-01-28 08:07 | 4550 | 1900-01-24 | 1900-01-15 17:48 | 0.5625 | 0.5 | 0.25 | 0.61875 | 0.23472 | 0.21736 | 0.57222 | 0.54167 | 0.44028 | 0.625 | 0.58333 | 0.52569 | 0.375 | 0.8375 | 0.48472 | 0.65903 | 0.57569 | 0.51111 | 0.69931 | 0.45208 | 0.6875 | 0.58125 | 0.34931 | 0.72569 | 0.64236 | 0.65486 | 0.2375 | 0.56736 | 0.72361 | 0.54028 | 0.76597
KANO EAST | 15MVA TR1 JOGANA | KAWAJI | 11KV TSAMIYA BABBA | D | 0.33333 | 8 | 1 | 1900-01-29 | 5550 | 1900-01-09 | 1900-01-13 17:02 | 0.48889 | 0.47778 | 0.31389 | 0.625 | 0.23472 | 0.16667 | 0.57222 | 0.54167 | 0.66667 | 0.625 | 0.58333 | 0.45069 | 0.375 | 0.81389 | 0.40556 | 0.65903 | 0.63125 | 0.51111 | 0.69931 | 0.35625 | 0.37431 | 0.74306 | 0.34931 | 0.38819 | 0.38056 | 0.28194 | 0.15625 | 0 | 0.53194 | 0.54028 | 0.76597
KANO EAST | 7.5MVA TR1 WUDIL | WUDIL | 11KV MAKAMA | C | 0.5 | 12 | 2.1 | 1900-01-28 15:11 | 4000 | 1900-01-14 | 1900-01-19 22:12 | 0.45833 | 0.375 | 0.5 | 0.54167 | 0.53125 | 0.76042 | 0.4375 | 0.73194 | 0.80208 | 0.875 | 0.66667 | 0.625 | 0.76667 | 0.98194 | 0.70833 | 0.91667 | 0.66667 | 0.38194 | 0.91667 | 0.58333 | 0.69306 | 0.86736 | 0.55347 | 0.83333 | 0.86111 | 0.94444 | 0.41667 | 0.375 | 0.54236 | 0.87639 | 0.73472
KANO EAST | 7.5MVA TR1 WUDIL | WUDIL | 11KV KUT | A | 0.83333 | 20 | 0.2 | 1900-01-29 | 2100 | 1900-01-24 | 0
KANO EAST | 7.5MVA TR1 WUDIL | WUDIL | 11KV WUDIL COMMERCIAL |  |  | 0 |  | 1900-01-29 |  | 0 | 1900-01-11 18:28 | 14: 0.98889; 15: 0.92708; 16: 0.93403; 17: 0.69236; 18: 1899-12-31; 19: 1899-12-31; 20: 0.625; 21: 0.80833; 22: 0.87431; 23: 0.58819; 24: 0.91597; 25: 0.86667; 29: 0.81944; 30: 0.98958; 31: 0.73958
KANO EAST | 15MVA TR1 KAWAJI | KAWAJI | 11KV DAKATA | B | 0.66667 | 16 | 3.3 | 1900-01-28 23:13 | 13050 | 1900-01-19 | 1900-01-16 18:38 | 0.56944 | 0.26319 | 0.51389 | 0.22569 | 0.70833 | 0.29167 | 0.57222 | 0.71944 | 0.5 | 0.89375 | 0.64306 | 0.81528 | 0.80139 | 0.68264 | 0.6625 | 0.75069 | 0.75208 | 0.19097 | 0.68542 | 0.41111 | 0.66528 | 0.57847 | 0.50972 | 0.82986 | 0.55347 | 0.36111 | 0.39792 | 0.51736 | 0.60139 | 0.46875 | 0.64028
KANO EAST | 15MVA TR1 KAWAJI | KAWAJI | 11KV YANKABA | B | 0.66667 | 16 | 3 | 1900-01-28 15:38 | 8300 | 1900-01-19 | 1900-01-17 06:43 | 0.56944 | 0.26319 | 0.40417 | 0.25 | 0.70833 | 0.34722 | 0.57222 | 0.73889 | 0.65347 | 0.89375 | 0.64306 | 0.81528 | 0.80139 | 0.70486 | 0.69931 | 0.69444 | 0.70347 | 0.45417 | 0.73611 | 0.43403 | 0.66528 | 0.60486 | 0.50972 | 0.82708 | 0.58958 | 0.29722 | 0.39792 | 0.58194 | 0.61042 | 0.46875 | 0.64028
KANO CENTRAL | 15MVA TR1 BRISCOE | BOMPAI | 11KV MAIMALARI | A | 0.83333 | 20 | 1.7 | 1900-01-28 11:19 | 850 | 1900-01-24 | 1900-01-20 11:06 | 0.75 | 0.63472 | 0.56528 | 0.49167 | 0.56806 | 0.71667 | 0.81736 | 0.40417 | 0.86528 | 1899-12-31 | 0.77014 | 0.72083 | 0.29931 | 0.95139 | 0.87639 | 0.84444 | 0.58333 | 0.10139 | 0.90069 | 0.48264 | 0.97361 | 0.83264 | 0.57778 | 0.75208 | 0.85347 | 0.71944 | 0.5375 | 0.58333 | 0.62014 | 0.67917 | 0.98958
KANO CENTRAL | 15MVA TR1 BRISCOE | SABON GARI | 11KV TUDUN WADA | D | 0.33333 | 8 | 3 | 1900-01-27 20:54 | 8400 | 1900-01-09 | 1900-01-13 21:38 | 0.32083 | 0.3125 | 0.56528 | 0.31319 | 0.38681 | 0.29167 | 0.81389 | 0.41667 | 0.86528 | 0.92778 | 0.77014 | 0.57431 | 0.43264 | 0.55556 | 0.41597 | 0.47014 | 0.50694 | 0.10347 | 0.49861 | 0.47917 | 0.49722 | 0.70833 | 0.43819 | 0.62361 | 0.56736 | 0.25 | 0.19583 | 0.21875 | 0.33194 | 0.15278 | 0.89653
KANO CENTRAL | 15MVA TR1 BRISCOE | BADAWA | 11KV YUSUF ROAD | A | 0.83333 | 20 | 2.7 | 1900-01-28 05:03 | 5900 | 1900-01-24 | 1900-01-20 14:31 | 0.75 | 0.63472 | 0.56528 | 0.54167 | 0.575 | 0.72014 | 0.81389 | 0.56736 | 0.86528 | 1899-12-31 | 0.77014 | 0.65903 | 0.30208 | 0.95139 | 0.87639 | 0.84444 | 0.64583 | 0.46875 | 0.87222 | 0.48264 | 0.97361 | 0.82778 | 0.57778 | 0.75208 | 0.98472 | 0.69514 | 0.57083 | 0.25 | 0.62014 | 0.45694 | 0.98958
KANO CENTRAL | 15MVA TR2 BRISCOE | BOMPAI | 11KV INDEPENDENCE | B | 0.66667 | 16 | 2.2 | 1900-01-28 06:54 | 13865 | 1900-01-19 | 1900-01-17 15:18 | 0.72986 | 0.56319 | 0.56528 | 0.39792 | 0.575 | 0.5 | 0.24306 | 0.56736 | 0.86528 | 1899-12-31 | 0.77014 | 0.72292 | 0 | 0.12986 | 0.67986 | 0.18611 | 0.65625 | 0.46875 | 0.90069 | 0.48264 | 0.90278 | 0.83333 | 0.57778 | 0.75208 | 0.66667 | 0.69514 | 0.53472 | 0.86319 | 0.58194 | 0.23611 | 0.98958
KANO CENTRAL | 15MVA TR2 BRISCOE | SABON GARI | 11KV GWAGWARWA | D | 0.33333 | 8 | 4.7 | 1900-01-28 04:25 | 10200 | 1900-01-09 | 1900-01-14 01:16 | 0.24653 | 0.38542 | 0.46944 | 0.48125 | 0.36736 | 0.25 | 0.56319 | 0.56736 | 0.70833 | 0.91667 | 0.77014 | 0.48472 | 0 | 0.50694 | 0.3375 | 0.55972 | 0.54306 | 0.41667 | 0.40833 | 0.47917 | 0.52778 | 0.62361 | 0.45625 | 0.60278 | 0.70347 | 0.27639 | 0.17014 | 0.54167 | 0.26875 | 0.45694 | 0.96319
KANO CENTRAL | 15MVA TR3 BRISCOE | BOMPAI | 11KV BOMPAI | A | 0.83333 | 20 | 1.8 | 1900-01-29 | 12500 | 1900-01-24 | 1900-01-21 00:52 | 0.56875 | 0.63472 | 0.57153 | 0.625 | 0.575 | 0.71597 | 0.81389 | 0.56736 | 0.86528 | 1899-12-31 | 0.77014 | 0.72292 | 0.41667 | 0.78056 | 0.87431 | 0.84444 | 0.47222 | 0.46875 | 0.90069 | 0.48264 | 0.97361 | 0.79028 | 0.57778 | 0.67361 | 0.97778 | 0.71944 | 0.59375 | 0.75 | 0.62014 | 0.69931 | 0.98958
KANO CENTRAL | 7.5MVA TR1 NIPP PRP | SABON GARI | 11KV KAURA GOJE | D | 0.33333 | 8 | 2.3 | 1900-01-28 12:50 | 5700 | 1900-01-09 | 1900-01-10 16:26 | 0.30764 | 0.375 | 0.40903 | 0 | 0.33333 | 0.44167 | 0.15139 | 0.65208 | 0.54167 | 0.85764 | 0.45833 | 0.35556 | 0.092361 | 0.41528 | 0.34097 | 0.22708 | 0.5 | 0.19375 | 0.44444 | 0.28542 | 0.54097 | 0.33472 | 0.25903 | 0.75764 | 0.40833 | 0.39514 | 0.21667 | 0.083333 | 0.35347 | 0.1875 | 0.76528
KANO CENTRAL | 7.5MVA TR1 NIPP PRP | SABON GARI | 11KV AIRPORT ROAD | A | 0.83333 | 20 | 0.1 | 1900-01-28 12:23 | 850 | 1900-01-24 | 1900-01-14 18:53 | 0.58333 | 0.45833 | 0.48542 | 0.25 | 0.053472 | 0.44167 | 0.44028 | 0.49653 | 0.41667 | 0.76806 | 0.45833 | 0.5 | 0.064583 | 0.60278 | 0.32083 | 0.80625 | 0.72708 | 0.44167 | 0.83194 | 0.55556 | 0.7 | 0.69097 | 0.48403 | 0.31736 | 0.43056 | 0.55139 | 0.50139 | 0.33403 | 0.68681 | 0.41528 | 0.97222
KATSINA CENTRAL | 7.5MVA TR1 BICHI | KANKIA | 11KV BICHI TOWN | C | 0.5 | 12 | 0.8 | 1900-01-29 | 2550 | 1900-01-14 | 1900-01-02 13:28 | 0 | 0 | 0 | 0.35694 | 0.077083 | 0.21528 | 0 | 0 | 0.069444 | 0.25 | 0.18542 | 0.041667 | 0.18056 | 0.35069 | 0 | 0.094444 | 0 | 0 | 0.125 | 0.065278 | 0.10417 | 0.35417 | 0.010417 | 0 | 0.21528 | 0.3125 | 0.11319 | 0.09375 | 0 | 0.03125 | 0.31458
KANO NORTH | 15MVA TR2 BUK | RIJIYAR ZAKI | 11KV GWARZO ROAD | A | 0.83333 | 20 | 0 | 1900-01-27 08:35 | 450 | 1900-01-24 | 1900-01-10 07:16 | 0.60069 | 0.16667 | 0.52986 | 0.066667 | 0.30556 | 0.78194 | 0.23194 | 0.39931 | 0.81528 | 0.44861 | 0.97569 | 0 | 0 | 0 | 0.40694 | 0.43472 | 0.10417 | 0.083333 | 0.55208 | 0.35069 | 0.17361 | 0.58472 | 0.38472 | 0.70972 | 0.43611 | 0.36458 | 0.10139 | 0 | 0.13889 | 0.63542 | 0.51944
KANO NORTH | 15MVA TR1 BUK | RIJIYAR ZAKI | 11KV NEW SITE | A | 0.83333 | 20 | 0.4 | 1900-01-29 | 2000 | 1900-01-24 | 1900-01-09 18:03 | 0.60069 | 0.44444 | 0.52986 | 0.066667 | 0.30556 | 0.67083 | 0.070833 | 0.39931 | 0.54167 | 0.375 | 0.71944 | 0 | 0 | 0 | 0.46111 | 0.42778 | 0.10417 | 0.083333 | 0.55208 | 0.35069 | 0.17361 | 0.58472 | 0.38472 | 0.70972 | 0.43611 | 0.36458 | 0.10139 | 0 | 0.13889 | 0.63542 | 0.51944
JIGAWA NORTH | 7.5MVA TR1 HADEJIA | HADEJIA | 11KV MAJE | C | 0.5 | 12 | 4.2 | 1900-01-26 21:07 | 16500 | 1900-01-14 | 1900-01-17 09:46 | 0.54167 | 0.375 | 0.64583 | 0.91667 | 0.91667 | 0.30556 | 0.34722 | 0.83333 | 0.8125 | 0.81181 | 0.75 | 0.51042 | 0.47917 | 0.70833 | 0.54167 | 0.75 | 0.83333 | 0.10764 | 0.75 | 0.60278 | 0.64931 | 0.66667 | 0.425 | 0.42361 | 0.375 | 0.58681 | 0.375 | 0.91736 | 0.45833 | 0.55764 | 0.43264
JIGAWA NORTH | 7.5MVA TR2 HADEJIA | HADEJIA | 11KV SHAGARI | C | 0.5 | 12 | 1.2 | 1900-01-29 | 4750 | 1900-01-14 | 1900-01-17 19:47 | 0.54167 | 0.5 | 0.70833 | 0.81736 | 0.91667 | 0.45833 | 0.26389 | 0.79167 | 0.83333 | 0.76875 | 0.83333 | 0.67917 | 0.85556 | 0.75 | 0.54167 | 0.75 | 0.83333 | 0.10764 | 0.83333 | 0.42222 | 0.20833 | 0.79167 | 0.15625 | 0.083333 | 0.48611 | 0.70833 | 0.65833 | 0.92639 | 0.45833 | 0.55764 | 0.58333
JIGAWA NORTH | 7.5MVA TR2 NIPP HADEJIA | HADEJIA | 11KV JAMAARE | D | 0.33333 | 8 | 3.3 | 1900-01-29 | 5000 | 1900-01-09 | 1900-01-20 16:31 | 0.44653 | 0.58333 | 0.72569 | 0.95833 | 0.76806 | 0.54861 | 0.43472 | 0.81944 | 0.30139 | 0.3125 | 0.53194 | 0.97917 | 0.97569 | 0.75694 | 1899-12-31 | 0.70833 | 0.25208 | 0.27083 | 0.92222 | 0.45486 | 0.75 | 0.95833 | 0.625 | 1899-12-31 | 0.88542 | 0.83333 | 0.53819 | 1899-12-31 | 0.91667 | 0.75139 | 0.67917
JIGAWA NORTH | 7.5MVA TR1 NIPP HADEJIA | HADEJIA | 11KV FANTAI | B | 0.66667 | 16 | 0.08 | 1900-01-29 |  | 1900-01-19 | 1900-01-23 00:10 | 0.89653 | 0.98611 | 1899-12-31 | 0.81736 | 0.88194 | 0.54861 | 0.57639 | 0.52847 | 0.375 | 0.3125 | 0.82361 | 0.94028 | 0.97569 | 0.75694 | 0.89931 | 1899-12-31 | 1899-12-31 | 0.27083 | 0.92222 | 0.59514 | 0.83333 | 1899-12-31 | 0.625 | 0.91319 | 0.88542 | 0.91667 | 0.79861 | 0.625 | 0.91667 | 0.70833 | 0.67778
JIGAWA NORTH | 7.5MVA TR1 NIPP MALAMADORI | GUMEL | 11KV MAKWALLA | D | 0.33333 | 8 | 1.4 | 1900-01-28 17:05 | 3200 | 1900-01-09 | 1900-01-07 18:03 | 0.60694 | 0.68056 | 0.56597 | 0.625 | 0.49792 | 0.46736 | 0.26944 | 0.60833 | 0.89722 | 0.58333 | 0.55069 | 0.29167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4375 | 0.69444 | 0.97569
JIGAWA NORTH | 7.5MVA TR1 NIPP GUMEL | GUMEL | 11KV LAUTAI | C | 0.5 | 12 | 2.3 | 1900-01-29 | 7850 | 1900-01-14 | 1900-01-21 02:26 | 0.625 | 0.66667 | 0.63889 | 0.51944 | 0.66667 | 0.45 | 0.59375 | 0.66667 | 0.68681 | 0.66667 | 0.83333 | 0.83333 | 0.66667 | 0.77431 | 0.59514 | 0.91667 | 0.83333 | 0.35764 | 0.84028 | 0.56042 | 0.66667 | 0.83333 | 0.5 | 0.70833 | 0.91667 | 0.91667 | 0.6875 | 0.84722 | 0.84167 | 0.83333 | 0.95833
JIGAWA SOUTH | 7.5MVA TR1 DUTSE | DUTSE | 11KV GOVERNMENT HOUSE DUTSE | B | 0.66667 | 16 | 1.8 | 1900-01-29 | 14300 | 1900-01-19 | 1900-01-21 13:19 | 0.0069444 | 1899-12-31 | 1899-12-31 | 0.46875 | 0.98681 | 0.62014 | 0.47569 | 0.80764 | 0.875 | 0.5 | 0.86458 | 0.69583 | 0.41667 | 0.87431 | 0.70347 | 1899-12-31 | 0.64167 | 0.15972 | 0.87986 | 0.53403 | 1899-12-31 | 0.43125 | 0.60347 | 1899-12-31 | 0.57639 | 1899-12-31 | 0.76736 | 0.79028 | 1899-12-31 | 0.875 | 1899-12-31
JIGAWA SOUTH | 7.5MVA TR1 DUTSE | DUTSE | 11KV LIMAWA | C | 0.5 | 12 | 1.4 | 1900-01-28 12:59 | 4050 | 1900-01-14 | 1900-01-21 15:30 | 0.70833 | 1899-12-31 | 1899-12-31 | 0.68958 | 0.98681 | 0.58333 | 0.59028 | 0.79167 | 0.92639 | 0.5 | 0.92708 | 0.94931 | 0.82431 | 0.88125 | 0.53472 | 0.51597 | 0.64167 | 0.64167 | 0.89167 | 0.57361 | 0.5875 | 0.85278 | 0.59167 | 0.99028 | 0.71181 | 0.63264 | 0.45208 | 0.2875 | 0.93472 | 0.74653 | 0.70069
JIGAWA SOUTH | 7.5MVA TR1 DUTSE | DUTSE | 11KV GARU | C | 0.5 | 12 | 2.6 | 1900-01-29 | 12550 | 1900-01-14 | 1900-01-23 08:04 | 0.70833 | 1899-12-31 | 1899-12-31 | 0.81875 | 0.98681 | 0.58333 | 0.59028 | 0.79167 | 0.92639 | 0.5 | 0.92708 | 0.94931 | 0.82431 | 0.88125 | 0.79167 | 1899-12-31 | 0.64167 | 0.64167 | 0.89167 | 0.57361 | 0.5875 | 0.85278 | 0.59167 | 1899-12-31 | 0.71181 | 0.63264 | 0.50417 | 0.68125 | 1899-12-31 | 0.74653 | 1899-12-31
JIGAWA SOUTH | 7.5MVA TR1 DUTSE NIPP | DUTSE | 11KV SANI ABACHA WAY | B | 0.66667 | 16 | 1.4 | 1900-01-28 17:01 | 8550 | 1900-01-19 | 1900-01-23 05:12 | 0.75 | 1899-12-31 | 1899-12-31 | 0.80486 | 0.99653 | 0.62014 | 0.73958 | 0.80764 | 0.875 | 0.5 | 0.86458 | 0.83333 | 0.825 | 0.87431 | 0.78194 | 0.98611 | 0.64167 | 0.15972 | 0.87986 | 0.48472 | 1899-12-31 | 0.83403 | 0.58333 | 1899-12-31 | 0.66736 | 0.71528 | 0.75139 | 1899-12-31 | 1899-12-31 | 0.625 | 0.61528
JIGAWA SOUTH | 7.5MVA TR2 DUTSE NIPP | DUTSE | 11KV TAKUR | C | 0.5 | 12 | 0.7 | 1900-01-28 16:32 | 1200 | 1900-01-14 | 1900-01-22 07:37 | 0.52431 | 1899-12-31 | 1899-12-31 | 0.80486 | 0.97917 | 0.62014 | 0.47569 | 0.80764 | 0.875 | 0.5 | 0.86458 | 0.69583 | 0.41667 | 0.87431 | 0.70347 | 1899-12-31 | 0.64167 | 0.15972 | 0.87986 | 0.53403 | 1899-12-31 | 0.43125 | 0.60347 | 1899-12-31 | 0.57639 | 1899-12-31 | 0.76736 | 0.79028 | 1899-12-31 | 0.79167 | 1899-12-31
JIGAWA SOUTH | 7.5MVA TR1 BIRNIN KUDU | BIRNIN KUDU | 11KV SCHOOL OF NURSING | C | 0.5 | 12 | 4.6 | 1900-01-29 | 8300 | 1900-01-14 | 1900-01-04 16:24 | 0.38333 | 0.16667 | 0.47986 | 0.14792 | 0.021528 | 0.32986 | 0.083333 | 0.29167 | 0.16667 | 0.41667 | 0.16667 | 0.054167 | 0.15694 | 0.11389 | 0.080556 | 0.10069 | 0.40833 | 0.0097222 | 0.10486 | 0.041667 | 0.13403 | 0 | 0.0076389 | 0.17014 | 0.27153 | 0.33333 | 0.20833 | 0.33681 | 0.26944 | 0 | 0.22708
JIGAWA SOUTH | 7.5MVA TR1 BIRNIN KUDU | BIRNIN KUDU | 11KV MAJESTIC | B | 0.66667 | 16 | 0.7 | 1900-01-29 | 1000 | 1900-01-19 | 1900-01-04 16:24 | 0.38333 | 0.16667 | 0.47986 | 0.14792 | 0.021528 | 0.32986 | 0.083333 | 0.29167 | 0.16667 | 0.41667 | 0.16667 | 0.054167 | 0.15694 | 0.11389 | 0.080556 | 0.10069 | 0.40833 | 0.0097222 | 0.10486 | 0.041667 | 0.13403 | 0 | 0.0076389 | 0.17014 | 0.27153 | 0.33333 | 0.20833 | 0.33681 | 0.26944 | 0 | 0.22708
KATSINA NORTH | 15MVA TR1 IBB WAY KATSINA | KATSINA URBAN | 11KV GRA | C | 0.5 | 12 | 5.4 | 1900-01-29 | 22700 | 1900-01-14 | 1900-01-17 16:23 | 0.5 | 0.58333 | 0.54167 | 0.54167 | 0.5 | 0.5 | 0.5 | 0.70833 | 0.5 | 0.70833 | 0.66667 | 0.66667 | 0.5 | 0.375 | 0.67431 | 0.70833 | 0.875 | 0.70833 | 0.59028 | 0.41736 | 0.75 | 0.66667 | 0.54167 | 0.66667 | 0.58333 | 0.54236 | 0.70833 | 0.66667 | 0.58333 | 0.70833 | 0.5
KATSINA NORTH | 15MVA TR3 IBB WAY KATSINA | KATSINA URBAN | 11KV LOW COST | B | 0.66667 | 16 | 2.3 | 1900-01-28 21:33 | 8300 | 1900-01-19 | 1900-01-22 21:38 | 0.66667 | 0.5 | 0.41667 | 0.91667 | 0.875 | 0.79167 | 0.70833 | 0.83333 | 1899-12-31 | 0.95833 | 0.79167 | 0.66667 | 0.79167 | 0.79167 | 0.85278 | 0.625 | 0.91667 | 0.66667 | 0.91667 | 0.46528 | 0.875 | 0.75 | 0.58333 | 0.91667 | 0.91667 | 0.70833 | 0.83333 | 0.75 | 0.79167 | 0.91667 | 0.70833
KATSINA NORTH | 7.5MVA TR2 IBB WAY KATSINA | KATSINA CITY | 11KV KANO ROAD | C | 0.5 | 12 | 5.4 | 1900-01-28 13:29 | 4750 | 1900-01-14 | 1900-01-17 01:34 | 0.5 | 0.5 | 0.54167 | 0.25 | 0.5 | 0.54167 | 0.5 | 0.66667 | 0.5 | 0.83333 | 0.70833 | 0.70833 | 0.5 | 0.45833 | 0.63681 | 0.70833 | 0.70833 | 0.41667 | 0.59167 | 0.46181 | 0.75 | 0.70833 | 0.41667 | 0.70833 | 0.66667 | 0.58333 | 0.79167 | 0.58333 | 0.5 | 0.70833 | 0.41667
KATSINA NORTH | 15MVA TR1 IBB WAY KATSINA | KATSINA CITY | 11KV ARMY BARRACKS | D | 0.33333 | 8 | 6.4 | 1900-01-28 15:48 | 23250 | 1900-01-09 | 1900-01-12 06:42 | 0.33333 | 0.41667 | 0.375 | 0.33333 | 0.29167 | 0.5 | 0.41667 | 0.45833 | 0.33333 | 0.45833 | 0.45833 | 0.375 | 0.33333 | 0.41667 | 0.47569 | 0.54167 | 0.66667 | 0.58333 | 0.4625 | 0.46528 | 0.45833 | 0.29167 | 0.25 | 0.5 | 0.45833 | 0.50069 | 0.5 | 0.41667 | 0.5 | 0.41667 | 0.29167
KATSINA NORTH | 15MVA TR3 IBB WAY KATSINA | KATSINA URBAN | 11KV KOFAR MARUSA | D | 0.33333 | 8 | 4.7 | 1900-01-28 06:29 | 10650 | 1900-01-09 | 1900-01-11 09:54 | 0.33333 | 0.375 | 0.41667 | 0.41667 | 0.29167 | 0.41667 | 0.41667 | 0.45833 | 0.33333 | 0.45833 | 0.41667 | 0.41667 | 0.33333 | 0.33333 | 0.44514 | 0.375 | 0.41667 | 0.33333 | 0.50208 | 0.21389 | 0.5 | 0.41667 | 0.29167 | 0.45833 | 0.33333 | 0.37639 | 0.58333 | 0.45833 | 0.375 | 0.54167 | 0.375
KATSINA NORTH | 15MVA TR3 IBB WAY KATSINA | KATSINA URBAN | 11KV DANDAGORO | C | 0.5 | 12 | 3.7 | 1900-01-28 14:42 | 24950 | 1900-01-14 | 1900-01-16 16:48 | 0.5 | 0.45833 | 0.54167 | 0.54167 | 0.25 | 0.75 | 0.41667 | 0.70833 | 0.5 | 0.83333 | 0.70833 | 0.66667 | 0.5 | 0.54167 | 0.55208 | 0.66667 | 0.55208 | 0.54167 | 0.41736 | 0.46875 | 0.58333 | 0.66667 | 0.41667 | 0.58333 | 0.54167 | 0.58472 | 0.75 | 0.58333 | 0.54167 | 0.75 | 0.58333
KATSINA NORTH | 7.5MVA TR1 KOFAR GUGA KATSINA | KATSINA CITY | 11KV HOSPITAL ROAD | D | 0.33333 | 8 | 5 | 1900-01-29 | 13500 | 1900-01-09 | 1900-01-15 00:20 | 0.54167 | 0.375 | 0.54167 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.625 | 0.83333 | 0.58333 | 0.54167 | 0.79167 | 0.625 | 0.33333 | 0.375 | 0.29167 | 1899-12-31 | 0.625 | 0.5 | 0.33333 | 0.5 | 0.66667 | 0.54167 | 0.33333 | 0.5 | 0.41667 | 0.58333 | 0.5 | 0.5 | 0.79167 | 0.34722
KATSINA NORTH | 7.5MVA TR2 KOFAR GUGA KATSINA | KATSINA CITY | 11KV FMC | D | 0.33333 | 8 | 3 | 1900-01-29 | 6450 | 1900-01-09 | 1900-01-15 02:45 | 0.54167 | 0.41667 | 0.5 | 0.16667 | 0.5 | 0.375 | 0.41667 | 0.58333 | 0.95833 | 0.66667 | 0.5 | 0.70833 | 0.66667 | 0.58333 | 0.16667 | 0.25 | 1899-12-31 | 0.625 | 0.58333 | 0.33333 | 0.54167 | 0.54167 | 0.52083 | 0.375 | 0.41667 | 0.45833 | 0.54167 | 0.5 | 0.58333 | 0.70833 | 0.38542
KATSINA NORTH | 7.5MVA TR2 KOFAR GUGA KATSINA | KATSINA CITY | 11KV DUTSEN SAFE | D | 0.33333 | 8 | 4.2 | 1900-01-29 | 10400 | 1900-01-09 | 1900-01-15 16:05 | 0.5 | 0.41667 | 0.5 | 0.29167 | 0.41667 | 0.33333 | 0.45833 | 0.58333 | 0.95833 | 0.58333 | 0.58333 | 0.875 | 0.625 | 0.5 | 0.20833 | 0.33333 | 1899-12-31 | 0.54167 | 0.5 | 0.45833 | 0.46528 | 0.58333 | 0.52083 | 0.41667 | 0.41667 | 0.41667 | 0.625 | 0.54167 | 0.75 | 0.83333 | 0.43403
KATSINA NORTH | 7.5MVA TR1 KOFAR GUGA KATSINA | KATSINA CITY | 11KV NATSINTA | A | 0.83333 | 20 |  | 1900-01-29 |  | 1900-01-24 | 1900-01-21 18:23 | 0.54167 | 0.41667 | 0.5 | 0.375 | 0.875 | 0.95833 | 0.45833 | 0.75 | 0.95833 | 0.66667 | 0.875 | 0.75 | 0.58333 | 0.95833 | 0.375 | 0.375 | 1899-12-31 | 0.625 | 1899-12-31 | 0.625 | 0.88542 | 1899-12-31 | 0.625 | 0.51597 | 0.875 | 0.75 | 0.98958 | 0.875 | 0.91667 | 1899-12-31 | 0.66667
KATSINA NORTH | 7.5MVA TR1 FADAMA NIPP | KATSINA URBAN | 11KV HASSAN USMAN ROAD | B | 0.66667 | 16 | 4.1 | 1900-01-28 02:57 | 26650 | 1900-01-19 | 1900-01-20 16:03 | 0.625 | 0.45833 | 0.625 | 0.20833 | 0.66667 | 0.875 | 0.70833 | 0.58333 | 0.75 | 0.875 | 0.70833 | 0.75 | 0.70833 | 0.79167 | 0.79167 | 0.79167 | 0.875 | 0.625 | 0.91667 | 0.64375 | 0.58333 | 0.875 | 0.55764 | 0.58333 | 0.625 | 0.75 | 0.83333 | 0.77292 | 0.69444 | 1899-12-31 | 0.41667
KATSINA NORTH | 7.5MVA TR1 FADAMA NIPP | KATSINA CITY | 11KV APEX | A | 0.83333 | 20 | 0.2 | 1900-01-29 | 2000 | 1900-01-24 | 1900-01-25 08:22 | 0.875 | 0.58333 | 0.625 | 0.20833 | 1899-12-31 | 0.875 | 0.70833 | 1899-12-31 | 0.79167 | 1899-12-31 | 0.70833 | 0.875 | 0.95833 | 0.95833 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.83333 | 1899-12-31 | 0.64375 | 0.79167 | 0.91667 | 0.59931 | 0.95833 | 1899-12-31 | 0.95833 | 0.83333 | 0.81389 | 1899-12-31 | 1899-12-31 | 0.83333
KATSINA NORTH | 7.5MVA TR2 FADAMA NIPP | KATSINA URBAN | 11KV NAGOGGO | C | 0.5 | 12 |  | 1900-01-29 |  | 1900-01-14 | 1900-01-11 10:41 | 0.33333 | 0.375 | 0.41667 | 0.41667 | 0.29167 | 0.41667 | 0.41667 | 0.45833 | 0.33333 | 0.625 | 0.41667 | 0.41667 | 0.33333 | 0.33333 | 0.44514 | 0.375 | 0.41667 | 0.33333 | 0.5 | 0.20833 | 0.5 | 0.29167 | 0.25 | 0.5 | 0.33333 | 0.375 | 0.58333 | 0.45833 | 0.375 | 0.54167 | 0.375
KATSINA NORTH | 7.5MVA TR2 FADAMA NIPP | KATSINA URBAN | 11KV KADARKO | B | 0.66667 | 16 |  | 1900-01-29 |  | 1900-01-19 | 1900-01-20 16:03 | 0.625 | 0.45833 | 0.625 | 0.20833 | 0.66667 | 0.875 | 0.70833 | 0.58333 | 0.75 | 0.875 | 0.70833 | 0.75 | 0.70833 | 0.79167 | 0.79167 | 0.79167 | 0.875 | 0.625 | 0.91667 | 0.64375 | 0.58333 | 0.875 | 0.55764 | 0.58333 | 0.625 | 0.75 | 0.83333 | 0.77292 | 0.69444 | 1899-12-31 | 0.41667
KATSINA NORTH | 7.5MVA TR1 KOFAR SAURI NIPP | KATSINA CITY | 11KV MUHAMMED DIKKO | D | 0.33333 | 8 | 2.7 | 1900-01-29 | 7750 | 1900-01-09 | 1900-01-16 12:20 | 0.625 | 0.625 | 0.45833 | 0.17083 | 0.5 | 0.625 | 0.70833 | 0.91667 | 0.70833 | 0.875 | 0.66667 | 0.5 | 0.34375 | 0.66667 | 0.45139 | 0.26389 | 0.63403 | 0.29167 | 0.58333 | 0.39722 | 0.55139 | 0.625 | 0.625 | 0.625 | 0.58958 | 0.54167 | 0.58333 | 0.50417 | 0.52431 | 0.79167 | 0.54167
KATSINA CENTRAL | 7MVA TR1 NIPP MUSAWA | KANKIA | 11KV KOFAR FADA | D | 0.33333 | 8 | 0.6 | 1900-01-29 | 1350 | 1900-01-09 | 1900-01-06 14:09 | 0.097222 | 0.33333 | 0.58333 | 0.25903 | 0.065278 | 0.072917 | 0.38542 | 0.125 | 0.33333 | 0.16667 | 0.125 | 0.25 | 0.29167 | 0.47847 | 0.10903 | 0.090278 | 0.47153 | 0.13542 | 0.38194 | 0.19444 | 0.50833 | 0.20486 | 0.029861 | 0.16667 | 0.31111 | 0.29653 | 0.13819 | 0.47153 | 0.10347 | 0.10764 | 0.30208
KATSINA CENTRAL | 7MVA TR1 NIPP MUSAWA | KANKIA | 11KV MATAZU | D | 0.33333 | 8 | 0.6 | 1900-01-29 | 2850 | 1900-01-09 | 1900-01-06 09:19 | 0 | 0.22917 | 0.58333 | 0.25903 | 0.065278 | 0.072917 | 0.38542 | 0.125 | 0.33333 | 0.16667 | 0.125 | 0.25 | 0.29167 | 0.47847 | 0.10903 | 0.090278 | 0.47153 | 0.13542 | 0.38194 | 0.19444 | 0.50833 | 0.20486 | 0.029861 | 0.16667 | 0.31111 | 0.29653 | 0.13819 | 0.47153 | 0.10347 | 0.10764 | 0.30208
KATSINA CENTRAL | 7.5MVA TR1 KAZAURE | KANKIA | 11KV KANTI | C | 0.5 | 12 | 1.1 | 2022-09-10 06:10 | 5350 | 1900-01-14 | 1900-01-17 04:41 | 0.56875 | 0.38403 | 0.70833 | 0.54861 | 0.58333 | 0.33194 | 0.41319 | 0.41667 | 0.65764 | 0.5 | 0.72569 | 0.93056 | 0.47708 | 0.32431 | 0.59653 | 0.57014 | 0.83333 | 0.73958 | 0.70972 | 0.50208 | 0.51389 | 0.33333 | 0.041667 | 0.92292 | 0.77222 | 0.47847 | 0.63819 | 0.94306 | 0.62153 | 0.77292 | 0.63542
KATSINA CENTRAL | 7.5MVA TR1 KAZAURE | KANKIA | 11KV DANTUNKU | C | 0.5 | 12 | 1.1 | 1900-01-29 | 3750 | 1900-01-14 | 1900-01-17 22:29 | 0.56875 | 0.38403 | 0.70833 | 0.54861 | 0.51389 | 0.40208 | 0.41319 | 0.41667 | 0.65764 | 0.5 | 0.72569 | 0.93056 | 0.47708 | 0.32431 | 0.59653 | 0.57014 | 0.83333 | 0.73958 | 0.70972 | 0.50208 | 0.79167 | 0.75 | 0.041667 | 0.92292 | 0.77222 | 0.47847 | 0.63819 | 0.85972 | 0.64792 | 0.79306 | 0.71875
KATSINA NORTH | 7.5MVA TR1 DAURA NIPP | DAURA | 11KV DAURAMA | B | 0.66667 | 16 | 2.4 | 1900-01-28 10:49 | 11750 | 1900-01-19 | 1900-01-23 01:08 | 0.83333 | 1899-12-31 | 0.79167 | 0.5 | 0.75 | 0.5 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.66667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.66667 | 0.75 | 0.41667 | 0.70833 | 0.66667 | 0.54167 | 0.75 | 0.54167 | 0.45833 | 0.75 | 0.75 | 0.71389 | 0.79167 | 0.58333
KATSINA NORTH | 7.5MVA TR2 DAURA NIPP | DAURA | 11KV BAYAJIDDA | B | 0.66667 | 16 | 2.6 | 1900-01-29 | 11100 | 1900-01-19 | 1900-01-22 11:00 | 0.91667 | 1899-12-31 | 0.75 | 0.20833 | 0.79167 | 0.625 | 0.91667 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.75 | 1899-12-31 | 1899-12-31 | 0.91667 | 1899-12-31 | 1899-12-31 | 0.58333 | 0.95833 | 0.875 | 0.41667 | 0.66667 | 0.41667 | 0.45833 | 0.79167 | 0.58333 | 0.54167 | 0.70833 | 0.58333 | 0.625 | 0.79167 | 0.58333
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV JABIRI | C | 0.5 | 12 | 4.6 | 1900-01-28 22:16 | 14350 | 1900-01-14 | 1900-01-19 08:04 | 0.50694 | 0.66667 | 0.58333 | 0.33333 | 0.83333 | 0.93472 | 0.675 | 0.85278 | 0.83333 | 0.79861 | 0.95833 | 0.875 | 0.70833 | 0.59861 | 0.69097 | 0.61111 | 0.22153 | 0.84167 | 0.72778 | 0.375 | 0.29167 | 0.625 | 0.54167 | 0.75 | 0.75 | 0.58333 | 0.65972 | 0.46667 | 0.375 | 0.83333 | 0.83333
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV DUTSEN REME | C | 0.5 | 12 | 2.8 | 1900-01-29 | 3050 | 1900-01-14 | 1900-01-21 00:25 | 0.54861 | 0.625 | 0.58333 | 0.45833 | 0.83333 | 0.93403 | 0.47639 | 0.85278 | 0.77569 | 0.79861 | 0.95833 | 0.875 | 0.70833 | 0.59861 | 0.69167 | 0.68542 | 0.60278 | 0.875 | 0.72778 | 0.375 | 0.70833 | 0.70833 | 0.45833 | 0.70833 | 0.58333 | 0.73958 | 0.79931 | 0.82778 | 0.66667 | 0.91667 | 0.91667
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV INDUSTRIAL | A | 0.83333 | 20 | 2 | 2022-09-02 19:30 | 4700 | 1900-01-24 | 1900-01-24 04:47 | 1899-12-31 | 0.95833 | 0.79167 | 1899-12-31 | 1899-12-31 | 0.95833 | 0.83333 | 0.85278 | 0.89097 | 0.69792 | 0.625 | 0.875 | 0.75 | 0.59583 | 0.65556 | 0.44306 | 0.60278 | 0.875 | 0.72778 | 0.375 | 0.83333 | 0.75 | 0.25 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.96944 | 0.97153 | 0.95833 | 1899-12-31 | 0.95833
KATSINA SOUTH | 7.5MVA TR1 KATSINA ROAD FUNTUA | FUNTUA | 11KV TOWN | C | 0.5 | 12 | 3.1 | 2022-09-02 09:55 | 6750 | 1900-01-14 | 1900-01-20 08:05 | 0.54861 | 0.58333 | 0.58333 | 0.625 | 1899-12-31 | 0.95833 | 0.80208 | 0.85278 | 0.70833 | 0.79861 | 0.95833 | 0.875 | 0.625 | 0.59861 | 0.65139 | 0.7875 | 0.60278 | 0.84583 | 0.72778 | 0.375 | 0.66667 | 0.54167 | 0.25 | 0.66667 | 0.83333 | 0.58333 | 0.575 | 0.5875 | 0.625 | 0.66667 | 0.83333
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV NAKOWA | C | 0.5 | 12 | 4.3 | 2145-04-20 01:48 | 11250 | 1900-01-14 | 1900-01-18 19:11 | 0.5 | 0.5 | 0.54167 | 0.45833 | 0.73611 | 0.58333 | 0.86111 | 0.64028 | 0.88264 | 0.89722 | 0.72153 | 1899-12-31 | 0.48056 | 0.56111 | 0.55069 | 0.42847 | 0.82917 | 0.90139 | 0.93264 | 0.47708 | 0.46736 | 0.50069 | 0.50556 | 0.82639 | 0.75694 | 0.71389 | 0.40903 | 0.35556 | 0.39722 | 0.39931 | 0.98403
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV MAI RUWA | E | 0.16667 | 4 | 1.3 | -0.22222 | 4150 | 1900-01-04 | 1900-01-19 23:10 | 0.27917 | 0.5 | 0.54167 | 0.40625 | 0.875 | 0.58333 | 0.5 | 0.20833 | 0.79931 | 0.89722 | 0.72153 | 0.97569 | 0.034722 | 0.56111 | 0.6875 | 0.91597 | 0.82847 | 0.90139 | 0.93264 | 0.47708 | 0.66528 | 0.55556 | 0.52639 | 1899-12-31 | 1899-12-31 | 0.71389 | 0.73611 | 0.55556 | 0.59722 | 1899-12-31 | 0.98889
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV FUNTUA TEXTILE MILL | A | 0.83333 | 20 | 1.6 | 1900-01-29 | 9000 | 1900-01-24 | 1900-01-23 15:45 | 1899-12-31 | 0.39931 | 0.85694 | 0.97778 | 1899-12-31 | 0.75 | 0.7625 | 0.64028 | 0.88264 | 0.89722 | 0.72153 | 1899-12-31 | 0.48056 | 0.56111 | 0.77986 | 0.91597 | 0.82847 | 0.90139 | 0.93264 | 0.47708 | 0.66528 | 0.65625 | 0.52639 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.875 | 0.56875 | 0.61042 | 1899-12-31 | 0.98889
KATSINA SOUTH | 15MVA TR1 TEXTILE JUNCTION FUNTUA | FUNTUA | 11KV FUNTUA WATER WORKS | A | 0.83333 | 20 | 0.6 | 1900-01-29 | 4500 | 1900-01-24 | 1900-01-22 08:18 | 0.51111 | 0.39931 | 0.85694 | 0.97778 | 0.77778 | 0.75 | 1899-12-31 | 0.64028 | 0.88264 | 0.89722 | 0.375 | 0.95833 | 0.125 | 0.56111 | 0.77986 | 0.91597 | 0.82917 | 0.90139 | 0.93264 | 0.47708 | 0.66528 | 0.65625 | 0.52639 | 1899-12-31 | 1899-12-31 | 1899-12-31 | 0.875 | 0.56875 | 0.61042 | 1899-12-31 | 0.89514
KATSINA SOUTH | 7.5MVA TR1 MALUMFASHI | MALUMFASHI | 11KV BCGA | C | 0.5 | 12 | 1.3 | 1900-01-29 | 6000 | 1900-01-14 | 1900-01-10 08:49 | 0.39792 | 0.34861 | 0.43333 | 0.26875 | 0.57153 | 0.65139 | 0.36806 | 0.625 | 0.8125 | 0.14653 | 0.39028 | 0.42708 | 0.0027778 | 0.44097 | 0.57292 | 0.30903 | 0.40972 | 0.39167 | 0.48542 | 0.19444 | 0.22708 | 0.30764 | 0.0069444 | 0.37361 | 0.27778 | 0.50486 | 0.69722 | 0.22708 | 0.26875 | 0.22847 | 0
KATSINA SOUTH | 7.5MVA TR1 MALUMFASHI | MALUMFASHI | 11KV GALADIMA | C | 0.5 | 12 | 1.7 | 1900-01-29 | 6300 | 1900-01-14 | 1900-01-10 11:30 | 0.39792 | 0.34861 | 0.43333 | 0.26875 | 0.57153 | 0.65139 | 0.36806 | 0.625 | 0.8125 | 0.14653 | 0.39028 | 0.41319 | 0.03125 | 0.52431 | 0.57292 | 0.30903 | 0.40972 | 0.39167 | 0.48542 | 0.19444 | 0.22708 | 0.30764 | 0.0069444 | 0.29028 | 0.27778 | 0.50486 | 0.69722 | 0.27569 | 0.31736 | 0.22847 | 0
Total | [7 empty] | #VALUE! | 3427188
[8 empty] | DATE | 30

## 1
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV JAHUN | TL |  |  | 2022-08-01 00:14 |  | E/F | OPENED DANTATA AND SHUARIN ISOLATORS | NO | 2022-08-01 11:16 |  | 11:02 | 0 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-01 00:36 | 3.5 | E/F | Tamburawa isolator was opened | NO | 2022-08-01 06:53 |  | 6:17 | 0.91632 |  |  | No
11KV TALAMIZ | TL |  |  | 2022-08-01 00:50 | 1.5 | E/F | Jogana town isolator was opened | NO | 2022-08-01 17:40 |  | 16:50 | 1.0521 |  |  | No
33KV MAMMAN NASIR | TL |  |  | 2022-08-01 02:10 | 0.6 | E/F | 33KV M/Nassir feeder was tried and stayed, nothing found. RE KTS was informed. | NO | 2022-08-01 09:35 |  | 7:25 | 0.18542 |  |  | No
33KV HADEJIA | TL |  |  | 2022-08-01 02:18 | 3.4 | E/F | Gidan leda leg was isolated | NO | 2022-08-01 11:54 |  | 9:36 | 1.36 |  |  | No
11KV GWARZO ROAD | TL |  |  | 2022-08-01 02:30 | 0.3 | E/F | 11KV Gwarzo Road feeder tripped on O/C all-phases and E/F 0.3MW. It was tried and stayed after isolated faculty of Science 500KVA due to punctured R-phase XLPE cable. TE R/Zaki approved. | YES | 2022-08-01 12:37 |  | 10:07 | 0.12646 |  |  | No
33KV KARAYE | TL |  |  | 2022-08-01 03:06 | 2.6 | E/F | Dangora isolator wasopened | NO | 2022-08-01 06:45 |  | 3:39 | 0.39542 |  |  | Yes
33KV CLUB | TL |  |  | 2022-08-01 04:51 | 5.6 | E/F | NOTHING FOUND | NO | 2022-08-01 08:38 |  | 3:47 | 0.88278 |  |  | Yes
33KV GANO | TL |  |  | 2022-08-01 04:57 | 6.6 | E/F | Gano 33KV feeder was tried and stayed after opened Polac isolator. RE KNE Hotoro approved. | NO | 2022-08-01 09:23 |  | 4:26 | 1.2192 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-01 05:27 | 1.3 | E/F | Tarau isolator was opened | NO | 2022-08-01 06:47 |  | 1:20 | 0.072222 |  |  | Yes
33KV FALGORE | TL |  |  | 2022-08-01 06:04 | 2.3 | E/F | K/Tudun wada isolator was opened | NO | 2022-08-01 06:46 |  | 0:42 | 0.067083 |  |  | Yes
11KV G.R.A. | TL |  |  | 2022-08-01 06:05 |  | E/F | Car wash isolator was oponed | NO | 2022-08-01 06:40 |  | 0:35 | 0 |  |  | #N/A
33KV CBN | TL |  |  | 2022-08-01 06:12 | 4.8 | E/F | Halliru Akilu isolaror was opened | NO | 2022-08-01 06:53 |  | 0:41 | 0.13667 |  |  | Yes
11KV TALAMIZ | TL |  |  | 2022-08-01 07:05 |  | E/F | removed a bird on the lime at Kwasan Gwami and also tree trimming was conducted. | YES | 2022-08-01 17:40 |  | 10:35 | 0 |  |  | No
11KV G.R.A. | TL |  |  | 2022-08-01 09:42 | 1.5 | E/F | 11KV GRA feeder tried and stayed after bye pass 1no lightning arrestor B-phase at Green view Hotel at 300KVA. TE Urban approved. | YES | 2022-08-01 12:17 |  | 2:35 | 0.16146 |  |  | #N/A
11KV BANK ROAD | TL |  |  | 2022-08-01 09:50 | 3 | O/C | 11KV Bank Road feeder was tried and stayed, patrolled nothing found. TE HQ approved. | NO | 2022-08-01 13:20 |  | 3:30 | 0.4375 |  |  | Yes
11KV SANI MAINAGGE | TL |  |  | 2022-08-01 09:53 | 2.5 | E/F | 11kV S/Mainagge feeder after discovered Samaila 500kVA S/S isolate itself. | YES | 2022-08-01 13:44 |  | 3:51 | 0.40104 |  |  | Yes
11KV KOFAR NASSARAWA | TL |  |  | 2022-08-01 09:57 | 3.3 | E/F | 11KV K/Nassarawa feeder tried and stayed after amended Y-phase J&P Dan Dawaki 500KVA. TE City TSP approved. | YES | 2022-08-01 12:40 |  | 2:43 | 0.37354 |  |  | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-08-01 10:52 | 3.5 | E/F | 33KV B/Kudu feeder was tried and stayed after opened Danmasara isolator, RE JGS approved. | NO | 2022-08-01 14:43 |  | 3:51 | 0.56146 |  |  | Yes
33KV KARAYE | TL |  |  | 2022-08-01 13:24 | 3.9 | E/F | 33kV Karaye feeder was tried and stayed after opened Dangora isolator. RE Dangora approved. | NO | 2022-08-01 14:37 |  | 1:13 | 0.19771 |  |  | Yes
11KV KOFAR NASSARAWA | TL |  |  | 2022-08-01 13:37 | 2.9 | E/F | 11KV K/Nassarawa feeder was tried and stayed after separated twisted conductor Y&B phase at Kasuwar Rimi. TE City approved. | YES | 2022-08-01 14:30 |  | 0:53 | 0.10674 |  |  | Yes
11KV LIMAWA | TL |  |  | 2022-08-01 13:47 | 1 | O/C&E/F | REMOVED A BIRD ON THE AT JIGAWAR SARKI | YES | 2022-08-01 18:42 |  | 4:55 | 0.20486 |  |  | No
33KV JAHUN | TL |  |  | 2022-08-01 14:42 | 2.9 | E/F | Jahun 33kV fdr was tried & stayed after opened Shuwarin and Dantata isolators, RE JGS approved. | NO | 2022-08-01 17:09 |  | 2:27 | 0.29604 |  |  | Yes
11KV AIRPORT ROAD | TL |  |  | 2022-08-01 15:25 | 1.3 | O/C | TRANSIENT | TRANSIENT | 2022-08-01 15:37 |  | 0:12 | 0.010833 |  |  | Yes
11KV HOTORO | TL |  |  | 2022-08-01 17:31 |  | E/F | After patrol discovered Zagi Old 500KVA S/S dropped 2no J&P third one isolated | YES | 2022-08-01 20:57 |  | 3:26 | 0 |  |  | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-01 17:31 |  | O/C | ISOLATED 11KV HOTORO FOR LINE PATROL | YES | 2022-08-01 17:42 |  | 0:11 | 0 |  |  | Yes
11KV FAGGE | TL |  |  | 2022-08-01 17:42 | 1.9 | E/F | after patrol discovered Wapa Old 500KVA S/S dropped 2no J&P third one isolated | YES | 2022-08-01 19:27 |  | 1:45 | 0.13854 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-01 18:03 | 18 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-01 18:08 |  | 0:05 | 0.0625 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-01 19:01 | 9.7 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-01 19:10 |  | 0:09 | 0.060625 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-01 20:01 | 7.8 | E/F | After patrol discovered Yandodo 500KVA S/S dropped 2no J&P third one isolated. | YES | 2022-08-01 22:34 |  | 2:33 | 0.82875 |  |  | Yes
33KV KURNA | TL |  |  | 2022-08-01 20:20 | 10.2 | E/F | After amended Red phase J&P on Isiyaku Rabiu 500KVA S/S. | YES | 2022-08-01 21:46 |  | 1:26 | 0.60917 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-01 20:31 | 3.4 | E/F | After opened Zango isolator as suspected faulty segment. | YES | 2022-08-01 22:53 |  | 2:22 | 0.33528 |  |  | Yes
33KV MAMMAN NASIR | TL |  |  | 2022-08-01 21:38 | 1.7 | E/F | Tree trimming was conducted at Makurdi. | NO | 2022-08-02 10:22 |  | 12:44 | 0.90194 |  |  | No
33KV GARKO | TL |  |  | 2022-08-01 21:50 | 2.6 | E/F | removed a branch of tree that bridged the line @ Mawashi village | YES | 2022-08-02 03:24 |  | 5:34 | 0.60306 |  |  | Yes
33KV BIRNIWA | TL |  |  | 2022-08-01 21:58 | 0.8 | E/F | Garin magaji & Kasheguwa isolators were opened. | NO | 2022-08-02 11:49 |  | 13:51 | 0.46167 |  |  | No
33KV DANDUME | TL |  |  | 2022-08-01 22:20 | 2 | E/F | OPENED JABIRI ISOLATOR | NO | 2022-08-02 06:32 |  | 8:12 | 0.68333 |  |  | No
33KV FALGORE | TL |  |  | 2022-08-01 22:38 | 3.1 | E/F | After opened an isolator at Kwanar Tudun Wada as suspected faulty segment | YES | 2022-08-02 07:20 |  | 8:42 | 1.1237 |  |  | No
11KV KABUGA | SE |  |  | 2022-08-01 22:46 | 4.5 |  | Due to Dan - gwalalo 300KVA S/S on fire. S/S WAS ISOLATED | YES | 2022-08-02 23:13 |  | 24:27 | 4.5844 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-01 23:00 | 4 | E/F | NOTHING FOUND | NO | 2022-08-02 00:16 |  | 1:16 | 0.21111 |  |  | #N/A
33KV GAYA | TL |  |  | 2022-08-01 23:41 | 1.6 | E/F | KUT Isolator was opened | NO | 2022-08-02 00:26 |  | 0:45 | 0.05 |  |  | Yes
33KV WUDIL | TL |  |  | 2022-08-01 23:41 | 2.5 | E/F | 33KV GAYA Isolated for line patrol | NO | 2022-08-02 00:21 |  | 0:40 | 0.069444 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-01 23:42 | 5 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-02 23:38 |  | 23:56 | 4.9861 |  |  | No
33KV MAI ADUA | TL |  |  | 2022-08-01 23:45 | 2.4 | E/F | OPENED MAI ADUA ISOLATOR | NO | 2022-08-02 13:05 |  | 13:20 | 1.3333 |  |  | No
33KV MASHI | TL |  |  | 2022-08-01 23:48 | 2.6 | E/F | OPENED GODAI | NO | 2022-08-02 10:48 |  | 11:00 | 1.1917 |  |  | No
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 2
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV KAZAURE | TL |  |  | 2022-08-02 00:01 | 1 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-02 00:44 |  | 0:43 | 0.029861 |  |  | Yes
33KV BAGAUDA |  |  |  | 2022-08-02 00:02 | 6 | E/F | Opened Tamburawa isolator. | NO | 2022-08-02 12:30 |  | 12:28 | 3.1167
33KV LAW SCHOOL | TL |  |  | 2022-08-02 00:04 | 3.1 | E/F | After opened an isolator at Tarau as suspected faulty segment | NO | 2022-08-02 07:22 |  | 7:18 | 0.94292 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-02 00:31 | 2.7 | E/F |  |  |  |  | -44775.0215 | -120892.5581 |  |  | No
33KV MUSAWA | TL |  |  | 2022-08-02 00:47 | 3.2 | E/F |  |  |  |  | -44775.0326 | -143280.1044 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-02 00:56 | 2.8 | E/F | Patrolled nothing found along the line. | NO | 2022-08-02 12:02 |  | 11:06 | 1.295 |  |  | #N/A
33KV GUMEL | TL |  |  | 2022-08-02 01:02 | 0.8 | E/F | conducted tree trimming along the line | YES | 2022-08-02 15:15 |  | 14:13 | 0.47389 |  |  | No
33KV GANO | TL |  |  | 2022-08-02 01:07 | 7.5 | E/F | 33kV Gano feeder was tried and stayed after opened Budan, Indabo & Katai legs were opened. RE Hotoro approved. | NO | 2022-08-02 18:01 |  | 16:54 | 5.2813 |  |  | No
33KV SUMAILA | TL |  |  | 2022-08-02 01:11 | 1.7 | E/F | Opened Rungumau Isolator,. | NO | 2022-08-02 12:16 |  | 11:05 | 0.78507 |  |  | No
33KV DR. JAMIL GWAMNA | TL |  |  | 2022-08-02 01:45 |  |  | Repositioned R-phase pulled out conductor @ Dantata Junction, | YES | 2022-08-02 14:30 |  | 12:45 | 0 |  |  | #N/A
33KV KAZAURE | TL |  |  | 2022-08-02 02:11 | 2 | E/F | After tree trimming was conducted along the line. | YES | 2022-08-02 09:10 |  | 6:59 | 0.58194 |  |  | Yes
33KV HADEJIA | TL |  |  | 2022-08-02 02:18 | 3.4 | E/F | OPENED GIDAN LEDA ISOLATOR | NO | 2022-08-02 11:54 |  | 9:36 | 1.36 |  |  | No
33KV MTN | TL |  |  | 2022-08-02 02:24 | 9.4 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-02 02:35 |  | 0:11 | 0.071806 |  |  | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-08-02 03:31 | 2 | E/F | OPENED DANMASARA | NO | 2022-08-02 13:33 |  | 10:02 | 0.83611 |  |  | No
33KV DUTSE | TL |  |  | 2022-08-02 03:33 | 4 | E/F | Branch of tree that bridged the line @ Jarda | YES | 2022-08-02 12:42 |  | 9:09 | 1.525 |  |  | No
33KV ANGELS | TL |  |  | 2022-08-02 05:09 | 5.8 | E/F | Fire service isolator was opened. | NO | 2022-08-02 10:47 |  | 5:38 | 1.3614 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-02 05:25 | 8.5 | E/F | OPENED BOMPAI LEG | NO | 2022-08-02 12:39 |  | 7:14 | 2.5618 |  |  | No
33KV GAYA | TL |  |  | 2022-08-02 05:32 | 1.2 | O/C | OPENED KUT ISOLATOR | NO | 2022-08-03 16:35 |  | 35:03 | 1.7525 |  |  | No
33KV IDH | TL |  |  | 2022-08-02 06:30 | 13 | E/F | NOTHING FOUND | NO | 2022-08-02 13:52 |  | 7:22 | 3.9903 |  |  | No
33KV MTN | TL |  |  | 2022-08-02 06:31 | 10.7 | E/F | W. J Bush 300KVA S/S isolated due to 2no J&P dropped, Flour Mills 2.5MVA S/S dropped 2no J&P isolated & Silver Plastic 1MVA S/S dropped 3no J&P, RE S/Gari approved. | YES | 2022-08-02 15:03 |  | 8:32 | 3.8044 |  |  | No
33KV BUK | TL |  |  | 2022-08-02 06:37 |  | O/C | After opened an isolator at Kofar Famfo as suspected faulty segment. | NO | 2022-08-02 07:19 |  | 0:42 | 0 |  |  | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-02 06:43 | 26 | O/C | TRANSIENT | TRANSIENT | 2022-08-02 13:50 |  | 7:07 | 7.7097 |  |  | No
11KV AHMADU BELLO | TL |  |  | 2022-08-02 06:54 | 2.4 | E/F | after Dawaki Road isolator was opened. | YES | 2022-08-02 09:38 |  | 2:44 | 0.27333 |  |  | Yes
33KV KURNA | TL |  |  | 2022-08-02 06:59 | 9.2 | E/F | NOTHING FOUND | NO | 2022-08-02 11:34 |  | 4:35 | 1.7569 |  |  | Yes
33KV SPANISH 2 | TL |  |  | 2022-08-02 07:00 | 25 | O/C | NOTHING FOUND | NO | 2022-08-02 12:36 |  | 5:36 | 5.8333 |  |  | Yes
11KV NOMANS LAND | SE |  |  | 2022-08-02 07:05 |  | O/C | Due to conductor on the ground at Court road by Ballat Hedges. | YES | 2022-08-02 09:24 |  | 2:19 | 0 |  |  | #N/A
11KV JAKARA | TL |  |  | 2022-08-02 07:27 | 2.5 | E/F | After amended Y-phase J&P fuse at Sadiq 500kVA S/s. | YES | 2022-08-02 10:11 |  | 2:44 | 0.28472 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-02 07:35 | 6 | E/F | After halliru Akilu isolator was opened. | NO | 2022-08-02 09:25 |  | 1:50 | 0.45833 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-02 07:44 | 9.7 | E/F | OPENED JOGANA ISOLATOR | NO | 2022-08-02 12:40 |  | 4:56 | 1.9939 |  |  | Yes
11KV KANO ROAD | TL |  |  | 2022-08-02 09:30 | 4.1 | E/F | Amended Y-phase J&P fuse at ATC 500kVA. | NO | 2022-08-02 11:28 |  | 1:58 | 0.33597 |  |  | Yes
11KV DANDAGORO | TL |  |  | 2022-08-02 09:34 | 2.4 | E/F | Opened KATARDA isolator . | NO | 2022-08-02 12:32 |  | 2:58 | 0.29667 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-02 10:37 | 5.6 | E/F | OPENED FATIMA MUNZALI ISOLATOR | NO | 2022-08-02 13:35 |  | 2:58 | 0.69222 |  |  | Yes
WUDIL COMMERCIAL | TL |  |  | 2022-08-02 10:50 | 0.1 | E/F | Removed a branch of tree that bridged the line @ Sahaf Hotel, | YES | 2022-08-02 13:43 |  | 2:53 | 0.012014 |  |  | #N/A
33KV RIJIYAR ZAKI | SE |  |  | 2022-08-02 11:20 | 11.9 |  | Due to conductor on the ground at R/Zaki primary, LT conductor isolated | YES | 2022-08-02 11:52 |  | 0:32 | 0.26444 |  |  | Yes
33KV BUK | SE |  |  | 2022-08-02 11:29 | 13.2 |  | Due to conductor on the ground at R/Zaki primary.it was restored after cut conductor was confirmed on R/Zaki 33kV fdr. | NO | 2022-08-02 11:32 |  | 0:03 | 0.0275 |  |  | Yes
11KV AMINU KANO | TL |  |  | 2022-08-02 11:50 | 3.4 | E/F | FIRST UPRISER RETERMINATED R- PHASE | YES | 2022-08-04 11:45 |  | 47:55 | 6.7882 |  |  | No
33KV RIJIYAR ZAKI | SE |  |  | 2022-08-02 12:06 | 11.4 |  | Due to cut LT conductor on the ground @ Kadawa, amended | YES | 2022-08-02 13:03 |  | 0:57 | 0.45125 |  |  | Yes
33KV ANGELS | TL |  |  | 2022-08-02 12:16 | 4.7 | O/C | Star Seed 2.5MVA S/S dropped 3no J&P, Bagco Super sacks 1MVA S/S isolated 2no J&P dropped & K&H 1MVA S/S dropped 2no J&P isolated, | YES | 2022-08-02 13:02 |  | 0:46 | 0.15014 |  |  | Yes
11KV JAEN | TL |  |  | 2022-08-02 12:46 |  | O/C | amended R-phase J&P Makera 500KVA S/S | NO | 2022-08-02 15:33 |  | 2:47 | 0 |  |  | Yes
11KV TALAMIZ | TL |  |  | 2022-08-02 13:02 | 1.5 | E/F | NOTHING FOUND | NO | 2022-08-02 16:43 |  | 3:41 | 0.23021 |  |  | Yes
11KV ZAWACIKI | TL |  |  | 2022-08-02 13:04 |  | E/F | Removed a bird that bridged Y-phase with channel iron @ Ruga Fada & amended R-phase J&P @ Gaida 500KVA S/S, | YES | 2022-08-02 16:30 |  | 3:26 | 0 |  |  | Yes
11KV KOFAR NA'ISA | SE |  |  | 2022-08-02 13:30 | 4.4 |  | Due to Filin D.O 500KVA S/S on fire, restored after isolated Daneji 500KVA S/S due to punctured R&Y-phase XLPE cables | YES | 2022-08-02 15:14 |  | 1:44 | 0.31778 |  |  | #N/A
11KV KABUGA | SE |  |  | 2022-08-02 13:45 | 4.2 |  | Due to WTC 500KVA S/S on fire | YES | 2022-08-02 14:52 |  | 1:07 | 0.19542 |  |  | Yes
11KV FEDERAL SECRETARIAT | SE |  |  | 2022-08-02 13:50 |  |  | Due to cut conductor on the ground @ Federal Secretariat, It was discovered the cut conductor is on abundant project @ new filling station |  | 2022-08-02 15:05 |  | 1:15 | 0 |  |  | Yes
11KV AJASA | SE |  |  | 2022-08-02 14:20 | 2.3 | O/C | Removed a bird that bridged the line @ Gandu primary 500KVA S/S, | YES | 2022-08-02 16:08 |  | 1:48 | 0.1725 |  |  | Yes
11KV KUNDILA | TL |  |  | 2022-08-02 14:03 | 2.3 | O/C & E/F | 11KV Kundila feeder tried and stayed after Y-phase shattered disc insulator replaced @Ahmed Musa T-off. TE Hotoro approved. | YES | 2022-08-02 19:36 |  | 5:33 | 0.53187 |  |  | No
33KV MAI ADUA | TL |  |  | 2022-08-02 14:20 | 1.8 | E/F | OPENED MAIADUA, FAGO AND ZANGO LEGS | NO | 2022-08-02 20:27 |  | 6:07 | 0.45875 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-02 14:35 | 0 | E/F | Isolated the metering panel, | YES | 2022-08-02 15:45 |  | 1:10 | 0 |  |  | #N/A
11KV HAUSAWA | TL |  |  | 2022-08-02 14:36 | 1.3 | O/C & E/F | NOTHING FOUND | NO | 2022-08-02 16:56 |  | 2:20 | 0.12639 |  |  | Yes
33KV MAMMAN NASIR | TL |  |  | 2022-08-02 15:35 | 2.3 | E/F |  |  |  |  | -44775.6493 | -102983.9934 |  |  | No
11KV GWARZO ROAD | TL |  |  | 2022-08-02 15:37 | 0.1 | O/C & E/F | 11KV Gwarzo feeder tried and stayed patrolled nothing found. TE R/Zaki approved. | no | 2022-08-02 18:28 |  | 2:51 | 0.011875 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-02 15:51 | 14.4 | E/F | 33kV MTN feeder was tried and stayed after isolated Bebeji oil 500kVA S/S due to Heavy Sound Heard from the Metering Panel. RE S/Gari approved. | YES | 2022-08-02 18:12 |  | 2:21 | 1.41 |  |  | Yes
33KV MUSAWA | TL |  |  | 2022-08-02 15:54 | 2.9 | E/F |  |  |  |  | -44775.6625 | -129849.4212 |  |  | No
11KV MAJE | SE |  |  | 2022-08-02 16:50 | 2.8 | O/C | Due to pulled out conductor @ Yanguru village, LT conductor & isolated the faulty portion @ Masallacin Hamza 500KVA S/S, | NO | 2022-08-02 17:17 |  | 0:27 | 0.0525 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-02 17:10 | 17.6 | O/C & E/F | 33kV F/Mills feeder was tried and stayed after reposition Y Phase jumper resting on Channel iron at Rumawa. RE S/Gari approved. | NO | 2022-08-01 22:39 |  | -0.77153 | -13.5789 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-02 17:11 | 2.7 | O/C & E/F | 33kV Tamburawa feeder was tried and stayed after nothing found. RE Panshekara approved. | no | 2022-08-02 18:18 |  | 1:07 | 0.12562 |  |  | #N/A
33KV GASKIYA | TL |  |  | 2022-08-02 17:13 | 13.8 | O/C & E/F | DAKATA 11KV FDR ISOLATED FOR LINE PATROL | NO | 2022-08-02 17:28 |  | 0:15 | 0.14375 |  |  | Yes
11KV DAKATA | TL |  |  | 2022-08-02 17:13 |  | O/C & E/F | 11kV Dakata feeder was tried and stayed after separated twisted conductors at Nababa Badamasi Road. TE Kawaji approved. | YES | 2022-08-02 18:00 |  | 0:47 | 0 |  |  | Yes
33kv sumaila | TL |  |  | 2022-08-02 16:27 | 2.3 | E/F | Sumaila 33KV fdr was tried and stayed after opened Rungumau Isolator, RE JGS approved. | NO | 2022-08-02 19:19 |  | 2:52 | 0.27472 |  |  | Yes
33kv karaye | TL |  |  | 2022-08-02 17:09 | 3.7 | O/C & E/F | 33kV Karaye feeder was tried and stayed after opened Dangora isolator. RE Dangora approved. | NO | 2022-08-02 20:47 |  | 3:38 | 0.56014 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-02 17:10 | 2.1 | O/C & E/F | 33KV Law school feeder was tried and stayed after opened an isolator at Tarau as suspected faulty segment. RE KNW Dangora approved. | NO | 2022-08-02 20:49 |  | 3:39 | 0.31937 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-02 18:51 | 11.8 | O/C & E/F | 33KV MTN feeder tried and stayed after Nasiha Plastic 500KVA isolated itself. RE S/Gari approved. | YES | 2022-08-02 22:19 |  | 3:28 | 1.7044 |  |  | Yes
11KV TALAMIZ | TL |  |  | 2022-08-02 19:15 | 2.01 | O/C & E/F | [8/2, 21:46] K1 CENTRAL DISPATCH: @2122hrs - 33KV MTN feeder tried and failed after 2.5MVA Flour Mills and 1MVA Spinnal Tiles were opened. RE S/Gari approved. (OPENED JUMPER AT KWAKWACI | YES | 2022-08-04 06:14 |  | 34:59 | 2.9299 |  |  | No
33KV GASKIYA | TL |  |  | 2022-08-02 18:44 | 7.5 | O/C & E/F | NOTHING FOUND | NO | 2022-08-03 21:01 |  | 26:17 | 8.2135 |  |  | No
11KV MAJE | TL |  |  | 2022-08-02 19:38 | 3.1 | O/C | TREE TRIMMING WAS CONDUCTED ALONG YAN GURU ROAD | NO | 2022-08-03 15:46 |  | 20:08 | 2.6006 |  |  | No
33KV GARKO | TL |  |  | 2022-08-02 19:25 | 2.6 | E/F | OPENED DARKI AND JIGAWARE | NO | 2022-08-03 15:40 |  | 20:15 | 2.1938 |  |  | No
11KV HOTORO | SE |  |  | 2022-08-02 19:53 |  |  | 11KV Hotoro feeder tag due to conductor on ground at Tsamiyar Boka. TE Hotoro reported. Tag on 11KV Hotoro feeder was removed after faulty portion isolated. TE Hotoro reported | YES | 2022-08-02 22:15 |  | 2:22 | 0 |  |  | Yes | ABDURRASHID LAWAN.
11KV ORTHOPAEDIC | TL |  |  | 2022-08-02 20:03 |  | O/C | TRANSIENT | TRANSIENT | 2022-08-02 20:30 |  | 0:27 | 0 |  |  | Yes
11KV FANISAU | TL |  |  | 2022-08-02 20:05 |  | E/F | TREE TRIMMING WAS CONDUCTED ALONG THE LINE AND ALSO OPENED UNGOGO ISOLATOR | NO | 2022-08-04 22:40 |  | 50:35 | 0 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-02 19:55 |  | O/C | TRANSIENT | TRANSIENT | 2022-08-02 20:05 |  | 0:10 | 0 |  |  | Yes
11KV TAKUR | TL |  |  | 2022-08-02 12:50 |  | O/C | TRANSIENT | TRANSIENT | 2022-08-02 20:18 |  | 7:28 | 0 |  |  | No
33KV ANGELS | TL |  |  | 2022-08-02 20:43 | 11.9 | E/F | 33kV Angels feeder tried and stayed after 1MVA Agro Rubber isolated itself. RE KNI Zoo Road approved. | YES | 2022-08-02 22:13 |  | 1:30 | 0.74375 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-02 21:01 |  | O/C | 33KV Gaskiya feeder was tried and stayed after opened Bompai leg. RE Kawaji approved. | NO | 2022-08-02 21:26 |  | 0:25 | 0 |  |  | Yes
33KV MAMMAN NASIR | TL |  |  | 2022-08-02 15:35 | 2.3 | O/C & E/F | NOTHING FOUND | NO | 2022-08-02 20:46 |  | 5:11 | 0.49674 |  |  | Yes
33KV MAI ADUA | TL |  |  | 2022-08-02 14:20 | 1.8 | E/F | FAGO, SANDAMU AND ZANGO LEG WERE ISOLATED | NO | 2022-08-02 20:27 |  | 6:07 | 0.45875 |  |  | Yes
33KV SUMAILA | TL |  |  | 2022-08-02 21:09 | 1 | E/F | 33KV Sumaila feeder was tried and stayed after branch of tree removed at Dan masara qtrs, RE JGS approved. | YES | 2022-08-03 07:26 |  | 10:17 | 0.42847 |  |  | No
33KV SMALL SCALE | TL |  |  | 2022-08-02 21:20 | 19.5 | E/F | NOTHING FOUND | NO | 1/0/00 23:15 |  | #VALUE! | #VALUE! |  |  | #VALUE!
33KV DUTSENMA | TL |  |  | 2022-08-02 23:15 | 2.3 | E/F |  |  |  |  | -44775.9688 | -102984.7281 |  |  | No
33KV MUSAWA | TL |  |  | 2022-08-02 21:13 | 3.8 | E/F |  |  |  |  | -44775.884 | -170148.3593 |  |  | No
33KV DANGOTE | TL |  |  | 2022-08-02 21:27 | 14 | O/C | TRANSIENT | TRANSIENT | 2022-08-02 21:38 |  | 0:11 | 0.10694 |  |  | Yes
11KV MAIMALARI | TL |  |  | 2022-08-02 22:22 |  | O/C | NOTHING FOUND | NO | 2022-08-02 23:16 |  | 0:54 | 0 |  |  | Yes
11KV INDEPENDENCE | TL |  |  | 2022-08-02 22:22 |  | O/C | NOTHING FOUND | NO | 2022-08-02 23:15 |  | 0:53 | 0 |  |  | Yes
11KV TUDUN WADA | TL |  |  | 2022-08-02 22:22 |  | O/C | ISOLATED MAI TAKALMI 300KVA S/S DUE TO 2N0. J&P DROPPED | YES | 2022-08-03 22:13 |  | 23:51 | 0 |  |  | No
11KV GWAGWARWA | TL |  |  | 2022-08-02 23:36 | 2 | O/C | HAJ. FAIZA 500KVA S/S ISOLATED ITSELF | YES | 2022-08-03 19:11 |  | 19:35 | 1.6319 |  |  | No
33KV MTN | TL |  |  | 2022-08-02 22:39 | 3.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-02 22:49 |  | 0:10 | 0.026389 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-02 22:40 | 1.8 | E/F | OPENED KAFIN AGUR ISOLATOR | NO | 2022-08-03 09:30 |  | 10:50 | 0.8125 |  |  | No
11KV BACHIRAWA | TL |  |  | 2022-08-02 23:01 |  | E/F | HAJ. FAIZA 500KVA S/S ISOLATED ITSELF | YES | 2022-08-04 00:08 | [5 empty] | No
33KV NNPC | TL |  |  | 2022-08-02 23:04 | 5.6 | E/F | 33kV NNPC feeder was tried and stayed after opened Tinshama leg as suspected faulty segment. RE Hotoro approved. |  | 2022-08-03 01:30 | [5 empty] | No
33KV POLYTECHNIC | TL |  |  | 2022-08-02 23:08 | 3.5 | E/F | [8 empty] | No
33KV GANO | TL |  |  | 2022-08-02 23:43 | 5.3 | E/F | 33KV Gano feeder was tried and stayed after opened Polac isolator. RE KNE Hotoro approved. | NO | 2022-08-03 08:15 | [5 empty] | No

## 3
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
11KV YUSUF ROAD | TL |  |  | 2022-08-03 00:15 | 0.4 | E/F | NOTHING FOUND | NO | 2022-08-03 19:12 |  | 18:57 | 0.31583 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-03 00:07 | 4 | E/F | 33KV Bagauda feeder was tried and stayed after opened Tamburawa Isolator. RE Dangora approved. | NO | 2022-08-03 06:52 |  | 6:45 | 1.125 |  |  | No
33KV KURNA | TL |  |  | 2022-08-03 01:07 | 6.6 | E/F | NOTHING FOUND | NO | 2022-08-03 05:53 |  | 4:46 | 1.3108 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-03 01:12 | 5.5 | O/C & E/F | ISOLATED TANNERY 1MVA S/S DUE TO 2NO. J&P DROPPED. | NO | 2022-08-03 16:07 |  | 14:55 | 3.4184 |  |  | No
11KV IBRAHIM TAIWO | TL |  |  | 2022-08-03 01:18 |  | E/F | replaced shattered y phase disc insulator, also isolated zenith bank 500kva s/s due to 2no J&P Dropped | YES | 2022-08-03 19:23 |  | 18:05 | 0 |  |  | No
11KV TARAUNI | TL |  |  | 2022-08-03 01:25 | 1.8 | E/F | 11kV Tarauni feeder tried and stayed after Bashir Gumel 300KVA drop 1no J&P it was ammended. TE Hotoro approved. | YES | 2022-08-03 07:07 |  | 5:42 | 0.4275 |  |  | No
33KV SMALL SCALE | TL |  |  | 2022-08-03 01:50 | 4.3 | O/C & E/F | BRANCH OF TREE REMOVED AT HAWAN DAWAKI | YES | 2022-08-03 07:27 |  | 5:37 | 1.0063 |  |  | Yes
11KV AHMADU BELLO | TL |  |  | 2022-08-03 01:58 | 2.3 | O/C & E/F | 11KV Ahmadu Bello feeder tried and stayed after branch of tree removed at Malm Natsugune. TE HQ approved. | NO | 2022-08-03 08:10 |  | 6:12 | 0.59417 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-03 02:06 | 2.4 | O/C & E/F | NOTHING FOUND | NO | 2022-08-03 08:06 |  | 6:00 | 0.6 |  |  | #N/A
11KV GWARZO ROAD | TL |  |  | 2022-08-03 02:30 | 0.1 | O/C & E/F | REMOVED A BIRD THAT BRIDGED THE LINE AT BUK OLD SITE | YES | 2022-08-03 11:20 |  | 8:50 | 0.036806 |  |  | No
33KV BUK | TL |  |  | 2022-08-03 03:25 | 8.6 | O/C & E/F | NOTHING FOUND | NO | 2022-08-03 05:46 |  | 2:21 | 0.84208 |  |  | Yes
11KV BANK ROAD | TL |  |  | 2022-08-03 04:00 |  | O/C | 11KV Bank Road feeder was tried and stayed after Dr. Alkali Was opened TE HQ TSP approved. | NO | 2022-08-03 06:15 |  | 2:15 | 0 |  |  | Yes
11KV TOKARAWA | TL |  |  | 2022-08-03 05:03 | 1.4 | NO RI | Jumper opened at Tijjani T - Off as Suspected Faulty segment affecting 10No Substations | NO | 2022-08-03 08:23 |  | 3:20 | 0.19444 |  |  | Yes
33KV GAYA | TL |  |  | 2022-08-03 05:32 |  | O/C | OPENED KUT ISOLATOR | NO | 2022-08-03 16:35 |  | 11:03 | 0 |  |  | No
11KV KARKASARA | TL |  |  | 2022-08-03 04:36 | 3 | O/C & E/F | AMENDED PULLED OUT B- PHASE CONDUCTOR AT RYHAN STREET | YES | 2022-08-03 11:03 |  | 6:27 | 0.80625 |  |  | No
33KV DANBATTA | TL |  |  | 2022-08-03 00:31 | 2.1 | E/F |  |  |  |  | -44776.0215 | -94029.6452 |  |  | No
33KV SULE LAMIDO UNIVERSITY | TL |  |  | 2022-08-03 05:50 | 0.1 | E/F | OPENED GIDAN SUGAR ISOLATOR | NO | 2022-08-03 17:36 |  | 11:46 | 0.049028 |  |  | #N/A
33KV MASHI | TL |  |  | 2022-08-03 06:44 | 2.2 | E/F | OPENED GODAI ISOLATOR | NO | 2022-08-03 09:24 |  | 2:40 | 0.24444 |  |  | Yes
33KV FALGORE | TL |  |  | 2022-08-03 00:31 | 1.5 | E/F | 33KV Falgore feeder was tried and stayed after opened isolator at Kwanar Tudun Wada as suspected faulty segment. RE KNW Dangora approved. | NO | 2022-08-03 21:27 |  | 20:56 | 1.3083 |  |  | No
33KV FLOUR MILLS | TL |  |  | 2022-08-03 07:15 | 14.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 07:40 |  | 0:25 | 0.25347 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-03 07:20 | 6.3 | O/C & E/F | RE-OPENED GERAWA ISOLATOR | YES | 2022-08-03 07:40 |  | 0:20 | 0.0875 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-03 07:44 | 13 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 07:54 |  | 0:10 | 0.090278 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-03 08:41 | 13 |  | 33kV Dangote feeder was opened on Emergency with 13.0MW, due to B Phase Jumper touching concrete pole near BBY Super Sack Company. It was restored after opened A A Rano isolator, isolating faulty portion. RE KNI reported and approved. | YES | 2022-08-03 08:46 |  | 0:05 | 0.045139 |  |  | Yes
11KV TOWN | TL |  |  | 2022-08-03 06:54 | 1.6 | E/F | CONDUCTED TREE TRIMMING ALONG THE LINE. | YES | 2022-08-03 12:20 |  | 5:26 | 0.36222 |  |  | No
11KV MAKWALLA | TL |  |  | 2022-08-03 09:09 | 0.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 11:40 |  | 2:31 | 0.062917 |  |  | Yes
33KV KURNA | TL |  |  | 2022-08-03 09:18 | 10.7 | O/C & E/F | OPENED ABATTOIR ISOLATOR | NO | 2022-08-03 15:19 |  | 6:01 | 1.0529 |  |  | No
33KV AJIWA WATER WORKS | TL |  |  | 2022-08-03 10:25 | 4.2 | O/C & E/F | ISOLATED AJIWA WATER WORKS 2.5MVA S/S DUE TO PUNCTURED Y- PHASE XLPE CABLE | NO | 2022-08-03 11:20 |  | 0:55 | 0.099306 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-03 10:35 | 2.6 | E/F | REMOVED A BIRD THAT BRIDGED THE LINE AT BAKIN RUWA. | YES | 2022-08-03 13:14 |  | 2:39 | 0.38646 |  |  | #N/A
33KV GEZAWA | TL |  |  | 2022-08-03 10:57 | 3.5 | O/C & E/F | OPENED ZAURA DANBABA ISOLATOR | NO | 2022-08-03 11:52 |  | 0:55 | 0.13368 |  |  | Yes
33KV SMALL SCALE | TL |  |  | 2022-08-03 10:57 | 10.5 | O/C & E/F | GEZAWA 33KV FEEDER LEFT OUT FOR PATROL | NO | 2022-08-03 11:08 |  | 0:11 | 0.080208 |  |  | Yes
11KV KUNDILA | TL |  |  | 2022-08-03 10:04 |  | O/C & E/F | Amended R phase shattered Pin insulator at Kwana Shida T Off. | YES | 2022-08-03 22:10 |  | 12:06 | 0 |  |  | No
11KV KABUGA | TL |  |  | 2022-08-03 11:20 | 3.8 | O/C & E/F | AMENDED CUT Y- PHASE CONDUCTOR AT WTC QUARTERS | NO | 2022-08-03 17:06 |  | 5:46 | 0.91306 |  |  | No
11KV KARKASARA | TL |  |  | 2022-08-03 11:25 | 4.7 | O/C & E/F | NOTHING WAS FOUND | NO | 2022-08-03 15:07 |  | 3:42 | 0.72458 |  |  | Yes
11KV HASSAN USMAN ROAD | TL |  |  | 2022-08-03 11:47 | 3.1 | E/F | OPENED KANGIWA ISOLATOR |  | 2022-08-03 12:26 |  | 0:39 | 0.083958 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-03 12:15 | 6.5 | O/C | TRANSIENT |  | 2022-08-03 12:30 |  | 0:15 | 0.067708 |  |  | Yes
11KV MAKWALLA | SE |  |  | 2022-08-03 13:06 | 0.6 |  | DUE TO TILTED POLES WITHIN MALAM MADORI AS A RESULT OF HEAVY RAINFALL. Affected portion was isolated. | YES | 2022-08-03 17:30 |  | 4:24 | 0.11 |  |  | No
11KV NAKOWA | TL |  |  | 2022-08-03 12:20 | 3.2 | E/F | OPENED UNGUWAR DAHIRU ISOLATOR | NO | 2022-08-03 15:15 |  | 2:55 | 0.38889 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-03 13:52 | 6 | O/C & E/F | Opened Tinshama isolator. | NO | 2022-08-03 18:27 |  | 4:35 | 1.1458 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-03 14:03 | 16.7 | O/C & E/F | REPOSITINED PULLED OUT B- PHASE CONDUCTOR OPPITE DAURAMA PLASTIC. | YES | 2022-08-03 16:31 |  | 2:28 | 1.7164 |  |  | Yes
33KV SMALL SCALE | TL |  |  | 2022-08-03 14:06 | 9 | O/C & E/F |  |  |  |  | -44776.5875 | -402989.2875 |  |  | No
11KV JAKARA | TL |  |  | 2022-08-03 14:25 |  | O/C & E/F | Amended Y phase J&P at ladiyo 500KVA S/S. | YES | 2022-08-03 18:32 |  | 4:07 | 0 |  |  | No
33KV BUK | TL |  |  | 2022-08-03 14:33 | 10 | O/C & E/F | NOTHING FOUND | NO | 2022-08-03 15:38 |  | 1:05 | 0.45139 |  |  | Yes
11KV JAEN | TL |  |  | 2022-08-03 14:43 | 4.7 | O/C | NOTHING FOUND | NO | 2022-08-03 20:27 |  | 5:44 | 1.1228 |  |  | No
33KV JAHUN | TL |  |  | 2022-08-03 14:59 | 0.4 | E/F | Opened at Yalwawa area | NO | 2022-08-03 21:50 |  | 6:51 | 0.11417 |  |  | Yes
11KV HOTORO | SE |  |  | 2022-08-03 15:20 | 2.6 |  | DUE TO TSAMIYAR BOKA 300KVA S/S ON FIRE, REPORTED BY ABDULRAHMAN OF AKTH TSP. S/S ISOLATED | NO | 2022-08-03 17:58 |  | 2:38 | 0.28528 |  |  | Yes
11KV TOWN | TL |  |  | 2022-08-03 15:21 | 2.1 | E/F |  |  |  |  | -44776.6396 | -94030.9431 |  |  | No
11KV MAIMALARI | TL |  |  | 2022-08-03 16:12 |  | E/F | AMENDED 1 NO Y PHASE AT AA RANO 500KVA S/S | YES | 2022-08-03 19:20 |  | 3:08 | 0 |  |  | Yes
11KV INDEPENDENCE | TL |  |  | 2022-08-03 16:13 | 1 | E/F | NOTHING FOUND |  | 2022-08-03 19:03 |  | 2:50 | 0.11806 |  |  | Yes
11KV LIMAWA | SE |  |  | 2022-08-03 16:16 |  |  | DUE TO DISCREPANCY OBSERVED R=B =0.7 WHILE Y = 0.1MW. | NO | 2022-08-03 17:03 |  | 0:47 | 0 |  |  | Yes
33KV BUK | SE |  |  | 2022-08-03 16:18 | 10 |  | DUE TO FIRE OUTBREAK AT KABUGA THIRD GATE, REPORTED BY RE KNN KABUGA, ISOLATED 3NO. BURNT PREPAID METERS. |  | 2022-08-03 17:03 |  | 0:45 | 0.3125 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-03 16:42 | 7 | E/F | NOTHING FOUND | NO | 2022-08-03 18:49 |  | 2:07 | 0.61736 |  |  | Yes
11KV CHIRANCI | SE |  |  | 2022-08-03 16:44 | 4.8 |  | LT CONDUCTOR ON THE GROUND AT GADO DA MASU, REPORTEDBY YAHYA SABIU OF K1 | NO | 2022-08-03 17:56 |  | 1:12 | 0.24 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-03 17:06 | 0.6 | E/F | NOTHING FOUND | NO | 2022-08-04 15:03 |  | 21:57 | 0.54875 |  |  | No
11KV MAIDUGURI ROAD | TL |  |  | 2022-08-03 17:34 |  | O/C & E/F | OPENED YAN DODO ISOLATOR |  | 2022-08-04 08:58 |  | 15:24 | 0 |  |  | No
11KV FARAWA | TL |  |  | 2022-08-03 17:35 |  | O/C & E/F | Gerawa isolated due t 2No J&P dropped. | YES | 2022-08-03 20:24 |  | 2:49 | 0 |  |  | Yes
11KV AHMADU BELLO | TL |  |  | 2022-08-03 17:04 | 2.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 17:15 |  | 0:11 | 0.021389 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-03 17:45 | 15 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 17:56 |  | 0:11 | 0.11458 |  |  | Yes
33KV KARAYE | TL |  |  | 2022-08-03 17:55 | 3.5 | E/F | opened yalwan faki isolator | NO | 2022-08-03 19:38 |  | 1:43 | 0.25035 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-03 18:10 | 3.5 | E/F | TRANSIENT | TRANSIENT | 2022-08-03 18:26 |  | 0:16 | 0.038889 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-03 18:28 | 1 | E/F | TRANSIENT | TRANSIENT | 2022-08-03 18:26 |  | -0.0013889 | -0.0013889 |  |  | No
11KV JABIRI | TL |  |  | 2022-08-03 19:01 | 2.7 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 20:45 |  | 1:44 | 0.195 |  |  | Yes
11KV INDUSTRIAL | TL |  |  | 2022-08-03 19:30 | 0.8 | E/F |  |  |  |  | -44776.8125 | -35821.45 |  |  | No
33KV FALGORE | TL |  |  | 2022-08-03 19:36 | 2.9 | E/F | K/ TUDUNWADa isolatore opened | NO | 2022-08-04 08:55 |  | 13:19 | 1.6091 |  |  | No
33KV GARKO | TL |  |  | 2022-08-03 19:54 | 1.6 | E/F | Garko leg was isolated | YES | 2022-08-04 10:17 |  | 14:23 | 0.95889 |  |  | No
33KV TEXTILE | TL |  |  | 2022-08-03 19:58 | 0.8 | E/F | TEXTILE MILL 1.5MVA S/S ISOLATED | YES | 2022-08-03 20:45 |  | 0:47 | 0.026111 |  |  | Yes
33KV AJIWA WATER WORKS | TL |  |  | 2022-08-03 20:02 | 4.4 | E/F |  | NO | 2022-08-03 20:19 |  | 0:17 | 0.051944 |  |  | Yes
33KV KAITA | TL |  |  | 2022-08-03 20:15 | 2.4 | O/C & E/F | opened High Court and Kaita leg | NO | 2022-08-03 21:18 |  | 1:03 | 0.105 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-03 20:22 | 2.7 | E/F | OPENED BUK ISOLATOR | NO | 2022-08-03 21:18 |  | 0:56 | 0.105 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-03 20:42 | 5.9 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 20:52 |  | 0:10 | 0.040972 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-03 21:13 | 2.3 | E/F | Opened Tarau isolator, | NO | 2022-08-03 22:45 |  | 1:32 | 0.14694 |  |  | Yes
11KV BACHIRAWA | TL |  |  | 2022-08-03 21:16 |  | E/F | Re-posioned B-phase pull out conductor | YES | 2022-08-04 12:08 |  | 14:52 | 0 |  |  | No
11KV NOMANS LAND | TL |  |  | 2022-08-03 21:18 | 2 | E/F | NOTHING FOUND | NO | 2022-08-04 15:09 |  | 17:51 | 1.4875 |  |  | #N/A
11KV KABUGA | TL |  |  | 2022-08-03 21:20 | 5.4 | O/C & E/F | NOTHING FOUND | NO | 2022-08-04 15:03 |  | 17:43 | 3.9862 |  |  | No
33KV MAMMAN NASIR | TL |  |  | 2022-08-03 22:01 | 2.1 | E/F | nothin found | TRANSIENT | 2022-08-04 09:37 |  | 11:36 | 1.015 |  |  | No
33KV CBN | TL |  |  | 2022-08-03 22:02 | 4.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 22:12 |  | 0:10 | 0.03125 |  |  | Yes
11KV GWARZO ROAD | TL |  |  | 2022-08-03 22:08 | 0.2 | O/C & E/F | branch of tree was removed at BUK Staff school | YES | 2022-08-04 08:30 |  | 10:22 | 0.086389 |  |  | No
33KV KURNA | TL |  |  | 2022-08-03 22:29 | 8 | O/C | TRANSIENT | TRANSIENT | 2022-08-03 22:57 |  | 0:28 | 0.15556 |  |  | Yes
33KV KARAYE | TL |  |  | 2022-08-03 22:16 | 1.9 | E/F | OPENED DANGORA ISOLATOR | NO | 2022-08-03 06:40 |  | -0.65 | -1.235 |  |  | No
33KV MAI ADUA | TL |  |  | 2022-08-03 22:32 | 2 | E/F | Mai adua and Zango legs opened | NO | 2022-08-04 07:16 |  | 8:44 | 0.72778 |  |  | No
33KV MASHI | TL |  |  | 2022-08-03 22:38 | 1.4 | E/F | Godai line isolator was opened | NO | 2022-08-04 07:15 |  | 8:37 | 0.50264 |  |  | No
33KV KWANKWASO | TL |  |  | 2022-08-03 23:05 | 0.9 | E/F | OPENED BUK ISOLATOR | NO | 2022-08-04 10:10 |  | 11:05 | 0.41562 |  |  | No
33KV KURNA | SE |  |  | 2022-08-03 23:09 | 5 |  | Due to Discripancy observed, R = B = 5.0MW, Y = 0MW | YES | 2022-08-04 09:45 |  | 10:36 | 2.2083 |  |  | No
11KV HOTORO | TL |  |  | 2022-08-03 23:50 | 2.3 | E/F | CBN Qtr 500KVA S/S isolated it self. | YES | 2022-08-04 02:31 |  | 2:41 | 0.25715 |  |  | Yes
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 4
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV SUMAILA | TL |  |  | 2022-08-04 00:14 | 1.5 | E/F | Ringim Isolator was opened | NO | 2022-08-04 09:08 |  | 8:54 | 0.55625 |  |  | No
33KV GARKO | TL |  |  | 2022-08-05 00:25 | 1.8 | E/F | After Garko, Darki and Jigaware legs were isolated as suspected faulty segment. | NO | 2022-08-05 10:45 |  | 10:20 | 0.775 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-04 00:26 | 2.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 00:36 |  | 0:10 | 0.019444 |  |  | Yes
33KV KAZAURE | TL |  |  | 2022-08-04 00:46 | 1.2 | E/F | Tree trimming conducted along the line. | NO | 2022-08-04 07:12 |  | 6:26 | 0.32167 |  |  | Yes
11KV DAURAMA | TL |  |  | 2022-08-04 00:58 | 2 | O/C | TREE TRIMMING WAS CONDUCTED ALONG THE LINE | NO | 2022-08-04 11:55 |  | 10:57 | 0.9125 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-04 01:49 | 2.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 01:59 |  | 0:10 | 0.018056 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-04 01:50 | 3.5 | O/C & E/F | 500kva Usman bin Affan was isolated due to 2no J&P Dropped | NO | 2022-08-04 06:26 |  | 4:36 | 0.67083 |  |  | Yes
11KV MAJE | TL |  |  | 2022-08-04 04:04 | 2 | O/C & E/F | NOTHING FOUND | YES | 2022-08-04 10:33 |  | 6:29 | 0.54028 |  |  | No
11KV HASSAN USMAN ROAD | TL |  |  | 2022-08-04 04:23 | 2.6 | E/F | Kangiwa isolator was opened | NO | 2022-08-04 10:17 |  | 5:54 | 0.63917 |  |  | No
33KV BIRNIN KUDU | TL |  |  | 2022-08-04 04:29 | 0.5 | E/F | RURU ISOLATOR OPENED | NO | 2022-08-04 08:04 |  | 3:35 | 0.074653 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-04 04:30 | 14.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 04:42 |  | 0:12 | 0.12083 |  |  | Yes
11KV KANO ROAD | TL |  |  | 2022-08-04 04:56 | 2.3 | E/F | Amending D-fitting resting on C/iron @ 300kva mobil relief | YES | 2022-08-04 09:41 |  | 4:45 | 0.45521 |  |  | No
11KV G.R.A. | TL |  |  | 2022-08-04 05:01 | 2.3 | E/F | Opened Car wash isolator, | NO | 2022-08-04 07:09 |  | 2:08 | 0.20444 |  |  | #N/A
11KV KOFAR MARUSA | TL |  |  | 2022-08-04 05:02 | 1.6 | E/F | Branch of tree removed along the line | YES | 2022-08-04 09:16 |  | 4:14 | 0.28222 |  |  | No
33KV AJIWA WATER WORKS | TL |  |  | 2022-08-04 05:35 | 0.5 | E/F |  |  |  |  | -44777.2326 | -22388.6163 |  |  | No
33KV GUJUNGU | SE |  |  | 2022-08-04 06:40 | 0.2 |  | Due to fire outbreak at Gujungu 500KVA S/S, S/S WAS ISOLATED. | NO | 2022-08-04 18:21 |  | 11:41 | 0.097361 |  |  | No
33KV MAI ADUA | TL |  |  | 2022-08-04 07:55 | 1.1 | E/F | Fago, Sandamu and Karkarku legs isolated | NO | 2022-08-04 10:15 |  | 2:20 | 0.10694 |  |  | Yes
33KV SPANISH 2 | TL |  |  | 2022-08-04 07:55 | 16.3 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 08:19 |  | 0:24 | 0.27167 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-04 08:12 | 9 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 08:23 |  | 0:11 | 0.06875 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-04 08:17 | 5.3 | E/F | Tamburawa isolator was opened | NO | 2022-08-04 12:35 |  | 4:18 | 0.94958 |  |  | Yes
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-04 09:10 | 9.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 09:18 |  | 0:08 | 0.054444 |  |  | Yes
33KV MUSAWA | TL |  |  | 2022-08-04 09:35 | 0.1 | E/F | Bichi, Kusada,& Musawa legs opened | NO | 2022-08-04 14:32 |  | 4:57 | 0.020625 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-04 09:24 | 9 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 09:37 |  | 0:13 | 0.08125 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-04 09:48 | 6.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 09:48 |  | 0:00 | 0 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-04 10:05 | 2.5 | O/C & E/F | DR.Jamil was opened | NO | 2022-08-04 11:27 |  | 1:22 | 0.14236 |  |  | #N/A
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-04 10:51 | 11.7 | O/C | Gwazaje isolator was opened | NO | 2022-08-04 12:30 |  | 1:39 | 0.80438 |  |  | Yes
11KV LAMIDO | TL |  |  | 2022-08-04 10:22 | 4 | E/F | Gadar Yanmata S/S DUE to 3no J&P Dropped and replaced 2no. lightning arrestor | YES | 2022-08-04 17:21 |  | 6:59 | 1.1639 |  |  | No
11KV KARKASARA | TL |  |  | 2022-08-04 11:20 | 5 | O/C | TRANSIENT | YES | 2022-08-04 11:30 |  | 0:10 | 0.034722 |  |  | Yes
11KV KARKASARA | TL |  |  | 2022-08-04 11:30 |  | E/F | REPOSITIONED PULL OUT CONDUCTOR B-PHASE BEHIND ADO BAYERO ROYAL CITY | YES | 2022-08-04 15:04 |  | 3:34 | 0 |  |  | Yes
11KV AHMADU BELLO | TL |  |  | 2022-08-04 12:00 | 2.3 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 12:12 |  | 0:12 | 0.019167 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-04 12:15 | 14 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 12:26 |  | 0:11 | 0.10694 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-04 12:29 | 11.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 12:44 |  | 0:15 | 0.11979 |  |  | Yes
11KV FEDERAL SECRETARIAT | TL |  |  | 2022-08-04 12:40 | 3 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 12:50 |  | 0:10 | 0.020833 |  |  | Yes
11KV FEDERAL SECRETARIAT | TL |  |  | 2022-08-04 12:50 |  | E/F | Branch of tree removed at gwammaja | YES | 2022-08-04 15:13 |  | 2:23 | 0 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-04 13:20 | 3.2 | O/C & E/F | Garu isolator was opened | NO | 2022-08-04 17:34 |  | 4:14 | 0.56444 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-04 13:49 | 0.2 | E/F | Replaced shatted disc insulator Y phase near Awbel filling station | YES | 2022-08-05 17:44 |  | 27:55 | 0.23264 |  |  | No
33KV DANBATTA | TL |  |  | 2022-08-04 14:01 | 1 | E/F | Danbatta Leg isolated | NO | 2022-08-04 14:33 |  | 0:32 | 0.022222 |  |  | Yes
33KV GAGARAWA | TL |  |  | 2022-08-04 15:10 | 1.9 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 16:58 |  | 1:48 | 0.1425 |  |  | Yes
33KV MASHI | TL |  |  | 2022-08-04 15:16 | 1.6 | E/F | KAYAWA WAS ISOLATED | NO | 2022-08-04 17:33 |  | 2:17 | 0.15222 |  |  | Yes
33KV IDH | TL |  |  | 2022-08-04 15:15 | 6 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 15:35 |  | 0:20 | 0.083333 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-04 15:19 | 6.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 15:30 |  | 0:11 | 0.049653 |  |  | Yes
11KV NOMANS LAND | TL |  |  | 2022-08-04 15:10 | 1.7 | E/F | AMENDED B- PHASE J&P AT BOMA ROAD BY SARKIN YAKI 500KVA S/S. | YES | 2022-08-04 18:17 |  | 3:07 | 0.22076 |  |  | #N/A
33KV GEZAWA | TL |  |  | 2022-08-04 15:19 | 3.7 | E/F | opened Zauran Danbaba | NO | 2022-08-04 17:25 |  | 2:06 | 0.32375 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-04 15:32 | 2 | E/F | 33KV Jamilu gwabna was opened | NO | 2022-08-04 17:26 |  | 1:54 | 0.15833 |  |  | #N/A
33KV ANGELS | TL |  |  | 2022-08-04 15:37 | 11.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 15:52 |  | 0:15 | 0.11979 |  |  | Yes
33KV IDH | TL |  |  | 2022-08-04 16:01 | 6.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 16:10 |  | 0:09 | 0.040625 |  |  | Yes
11KV BANK ROAD | TL |  |  | 2022-08-04 16:05 | 3.5 | E/F | Dr. Alkali isolator was opened | NO | 2022-08-04 17:18 |  | 1:13 | 0.17743 |  |  | Yes
11KV TALAMIZ | TL |  |  | 2022-08-04 16:33 | 2 | E/F | REMOVED A BIRD THAT BRIDGED THE LINE AT ALKALI, OPENED JOGANA ISOLATOR. | YES | 2022-08-05 01:20 |  | 8:47 | 0.73194 |  |  | No
33KV LAW SCHOOL | TL |  |  | 2022-08-04 16:06 | 3.3 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 16:16 |  | 0:10 | 0.022917 |  |  | Yes
33KV KARAYE | TL |  |  | 2022-08-04 17:13 | 4.6 | E/F | OPENED DANGORA ISOLATOR | NO | 2022-08-04 18:22 |  | 1:09 | 0.22042 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-04 18:49 | 17 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 18:57 |  | 0:08 | 0.094444 |  |  | Yes
11KV NOMANS LAND | TL |  |  | 2022-08-04 18:50 | 3 | E/F | NOTHING FOUND | NO | 2022-08-04 23:05 |  | 4:15 | 0.53125 |  |  | #N/A
11KV KOFAR NA'ISA | SE |  |  | 2022-08-04 18:52 |  |  | DUE TO DISCREPANCY OBSERVED R=Y = 3.6MW WHILE B = 0MW. AMENDED CUT B- PHASE JUMPER AT KARMA. | YES | 2022-08-04 21:10 |  | 2:18 | 0 |  |  | #N/A
33KV BIRNIN KUDU | TL |  |  | 2022-08-04 18:50 | 4.3 | E/F | OPENED GWARAM LEG | NO | 2022-08-04 21:14 |  | 2:24 | 0.43 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-04 20:00 | 4.5 | E/F | OPENED BUK ISOLATOR | NO | 2022-08-04 22:47 |  | 2:47 | 0.52187 |  |  | Yes
11KV AHMADU BELLO | TL |  |  | 2022-08-04 20:42 | 2.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 20:52 |  | 0:10 | 0.017361 |  |  | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-08-04 21:14 | 2.8 | E/F | OPENED DANMASARA ISOLATOR | NO | 2022-08-04 22:33 |  | 1:19 | 0.15361 |  |  | Yes
11KV G.R.A. | TL |  |  | 2022-08-04 21:24 | 4.1 | E/F | OPENED CAR WASH ISOLATOR | NO | 2022-08-04 23:05 |  | 1:41 | 0.28757 |  |  | #N/A
33KV KURNA | TL |  |  | 2022-08-04 21:36 | 5 | E/F | NOTHING FOUND | NO | 2022-08-04 23:35 |  | 1:59 | 0.41319 |  |  | Yes
33KV KOFAR GUGA | TL |  |  | 2022-08-04 21:48 | 4 | E/F | OPENED ALKALAM UNIVERSITY ISOLATOR | NO | 2022-08-05 06:03 |  | 8:15 | 1.375 |  |  | No
33KV MAMMAN NASIR | TL |  |  | 2022-08-04 21:50 | 1.1 | E/F | NOTHING FOUND | NO | 2022-08-04 22:54 |  | 1:04 | 0.048889 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-04 22:30 | 9 | O/C | TRAnsient | TRANSIENT | 2022-08-04 22:39 |  | 0:09 | 0.05625 |  |  | Yes
33KV SUMAILA | TL |  |  | 2022-08-04 22:39 | 1.9 | E/F | After opened Ringumau isolator as suspected faulty segment. | NO | 2022-08-05 09:20 |  | 10:41 | 0.84576 |  |  | No
11KV NOMANS LAND | TL |  |  | 2022-08-04 23:10 | 1.7 | E/F | After tree trimming conducted along the line. | NO | 2022-08-05 17:02 |  | 17:52 | 1.2656 |  |  | #N/A
33KV LAW SCHOOL | TL |  |  | 2022-08-04 23:13 | 2.6 | E/F | OPENED TARAU ISOLATOR | NO | 2022-08-05 07:10 |  | 7:57 | 0.86125 |  |  | No
33KV FLOUR MILLS | TL |  |  | 2022-08-04 23:32 | 15.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-04 23:42 |  | 0:10 | 0.10764 |  |  | Yes
33KV MALUMFASHI | TL |  |  | 2022-08-04 23:52 | 2.1 | E/F | After Danja Leg was Isolated | NO | 2022-08-05 08:29 |  | 8:37 | 0.75396 |  |  | No
33KV KWANKWASO | TL |  |  | 2022-08-04 23:35 | 1.5 | O/C & E/F | After opened an isolator at Garu as suspected faulty segment. | YES | 2022-08-05 09:53 |  | 10:18 | 0.64375 |  |  | No
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 5
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV BAGAUDA | TL |  |  | 2022-08-05 00:10 | 3 | E/F | OPENED TAMBURAWA ISOLATOR | NO | 2022-08-05 07:26 |  | 7:16 | 0.90833 |  |  | No
33KV GARKO | TL |  |  | 2022-08-05 00:25 | 1.8 | E/F | OPENED DARKI AND JIGAWARE | NO | 2022-08-05 10:45 |  | 10:20 | 0.775 |  |  | No
33KV FALGORE | TL |  |  | 2022-08-05 00:44 | 2.4 | E/F | OPENED KWANAR T/WADA ISOLATOR | NO | 2022-08-05 07:25 |  | 6:41 | 0.66833 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-05 01:24 |  | O/C & E/F | OPENED ZAURAN DANBABA ISOLATOR | NO | 2022-08-05 08:07 |  | 6:43 | 0 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-05 03:13 | 4.4 | O/C & E/F | ISOLATED DR JAMIL 33KV FEEDER | NO | 2022-08-05 04:30 |  | 1:17 | 0.23528 |  |  | #N/A
33KV DR. JAMIL GWAMNA | TL |  |  | 2022-08-05 03:13 |  | E/F | After patrol discovered TIAMMING Rice Mill 2.5MVA S/S dropped 2no J&P third one isolated | YES | 2022-08-05 09:21 |  | 6:08 | 0 |  |  | #N/A
33KV KAITA | TL |  |  | 2022-08-05 06:20 | 4 | E/F | OPENED AJIWA AND KAITA LEGS | NO | 2022-08-05 07:58 |  | 1:38 | 0.27222 |  |  | Yes
11KV MAJE | TL |  |  | 2022-08-05 07:47 | 2.6 | O/C & E/F | After tree trimming was conducted along the line. | NO | 2022-08-05 12:23 |  | 4:36 | 0.49833 |  |  | No
33KV GASKIYA | TL |  |  | 2022-08-05 08:01 | 13.5 | O/C & E/F | NOTHING FOUND | NO | 2022-08-05 10:55 |  | 2:54 | 1.6313 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-05 08:17 | 2.8 | O/C & E/F | OPENED ZAURAN DAN BABA ISOLATOR | NO | 2022-08-05 10:55 |  | 2:38 | 0.30722 |  |  | Yes
33KV DANDUME | TL |  |  | 2022-08-05 08:16 | 3.3 | E/F | After Mahuta leg Isolated | NO | 2022-08-05 09:08 |  | 0:52 | 0.11917 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-05 09:20 | 14 | O/C | NOTHING FOUND | NO | 2022-08-05 09:05 |  | -0.010417 | -0.14583 |  |  | No
33KV NNPC | TL |  |  | 2022-08-05 09:25 | 13.2 | E/F | After opened Jogana isolator as suspected faulty segment. | NO | 2022-08-05 11:04 |  | 1:39 | 0.9075 |  |  | Yes
11KV MAR | TL |  |  | 2022-08-05 11:40 | 2.7 | O/C | After tree trimming was conducted along the line. | YES | 2022-08-05 13:32 |  | 1:52 | 0.21 |  |  | #N/A
33KV GASKI | TL |  |  | 2022-08-05 11:53 | 8.4 | E/F | After Nassarawa isolator opened. | NO | 2022-08-05 12:29 |  | 0:36 | 0.21 |  |  | #N/A
33KV SUMAI | TL |  |  | 2022-08-05 11:52 | 2.2 | E/F | After a branch of tree was removed from the line at Takai and also Rungumau isolator opened. The line was patrolled sequel to report of a branch of tree on the line. | YES | 2022-08-05 12:20 |  | 0:28 | 0.042778 |  |  | #N/A
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-05 12:01 | 2.1 | O/C & E/F | After opened an isolator of 11KV Tamburawa water plant due to Carbonised on Red and Blue phases of its metering panel | YES | 2022-08-05 12:39 |  | 0:38 | 0.055417 |  |  | #N/A
11KV TOKARAWA | TL |  |  | 2022-08-05 12:09 | 1.6 |  | After Mustapha Rice Mill 300KVA S/S as suspected faulty segment. | YES | 2022-08-05 12:52 |  | 0:43 | 0.047778 |  |  | Yes
11KV BANK | TL |  |  | 2022-08-05 13:03 | 2.7 | E/F | NOTHING FOUND | NO | 2022-08-05 |  | -0.54375 | -1.4681 |  |  | #N/A
33KV IDH | TL |  |  | 2022-08-05 13:01 | 8.8 | E/F | Hajj Camp isolator was opened | NO | 2022-08-05 16:43 |  | 3:42 | 1.3567 |  |  | Yes
33KV JODA | TL |  |  | 2022-08-05 13:24 | 0.1 | E/F | Y phase jumper amended touching C/Iron at the back of DKT T/S | YES | 2022-08-05 19:35 |  | 6:11 | 0.025764 |  |  | No
33KV TAMBURAWA W/WORKS | SE |  |  | 2022-08-05 12:48 | 0.7 |  | 132KV incomer breaker at Tamburawa T/S was opened on emergency due to serious oil leakage observed on 30/40MVA | YES | 2022-08-05 12:55 |  | 0:07 | 0.0034028 |  |  | #N/A
33KV COCA COLA | SE |  |  | 2022-08-05 12:48 | 12 |  | 132KV incomer breaker at Tamburawa T/S was opened on emergency due to serious oil leakage observed on 30/40MVA | YES | 2022-08-05 12:55 |  | 0:07 | 0.058333 |  |  | Yes
33KV BIRNIWA | TL |  |  | 2022-08-05 13:18 | 0.8 | E/F | Nothing found | NO | 2022-08-05 21:06 |  | 7:48 | 0.26 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-05 13:34 | 14.5 | E/F | AA Rano isolator was opened | NO | 2022-08-05 15:17 |  | 1:43 | 1.0372 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-05 14:55 | 8.5 | O/C | NOTHING FOUND | NO | 2022-08-05 15:03 |  | 0:08 | 0.047222 |  |  | Yes
11KV UNGUWA UKU | TL |  |  | 2022-08-05 14:53 | 3.9 | O/C | NOTHING FOUND | NO | 2022-08-05 |  | -0.62014 | -2.4185 |  |  | #N/A
33KV SUMAILA | TL |  |  | 2022-08-05 14:58 | 2.3 | E/F | 1st upriser was opened | NO | 2022-08-05 20:40 |  | 5:42 | 0.54625 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-05 15:08 | 4 | O/C | NOTHING FOUND | NO | 2022-08-05 15:17 |  | 0:09 | 0.025 |  |  | Yes
33KV KAFIN HAUSA | TL |  |  | 2022-08-05 15:22 | 0.8 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-05 |  | -0.64028 | -0.51222 |  |  | No
33KV GARKO | TL |  |  | 2022-08-05 15:30 | 1 | E/F | Amend Y-Phase j&p that dropped at 200kva jigaware T-off s/s | YES | 2022-08-05 18:15 |  | 2:45 | 0.11458 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-05 13:34 | 14.5 | E/F | After opened AA Rano and Kwanar Ganduje isolators as suspected faulty segment | YES | 2022-08-05 15:57 |  | 2:23 | 1.4399 |  |  | Yes
33KV MASHI | TL |  |  | 2022-08-05 15:24 | 0.2 | E/F | Godai leg was isolated | NO | 2022-08-05 20:20 |  | 4:56 | 0.041111 |  |  | Yes
11KV MARHABA | TL |  |  | 2022-08-05 15:45 | 2.5 | O/C | After patrol discovered Masallacin Murtala 500KVA S/S dropped 2no J&P third one isolated. | YES | 2022-08-05 16:16 |  | 0:31 | 0.053819 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-05 16:07 | 5 | E/F | Tamburawa isolator was opened | NO | 2022-08-05 18:29 |  | 2:22 | 0.49306 |  |  | Yes
33KV GANO | TL |  |  | 2022-08-05 16:15 | 7 | E/F | Polac isolator was opened | NO | 2022-08-05 18:18 |  | 2:03 | 0.59792 |  |  | Yes
11KV U/UKU | SE |  |  | 2022-08-05 18:45 | 4 |  | Due to burnt B-Phase XLPE Cable |  | 2022-08-05 18:45 |  | 0:00 | 0 |  |  | #N/A
33KV IDH | TL |  |  | 2022-08-05 13:01 | 4 | E/F | After opened an isolator at Hajj camp as suspected faulty segment. | NO | 2022-08-05 16:43 |  | 3:42 | 0.61667 |  |  | Yes
33KV FLOUR MILLS | PM | 2022-08-05 16:30 | 2022-05-08 17:00 | 2022-08-05 17:01 |  |  | For safe working space to amend cut jumper at Dantata plastic. |  | 2022-08-05 17:50 |  | 0:49 | 0 | No | 2136:19
33KV GARKO | TL |  |  | 2022-08-05 16:55 | 6.7 | E/F | jigaware amended y- phase J&P | YES | 2022-08-05 18:15 |  | 1:20 | 0.37222 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-05 17:21 | 12.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-05 17:37 |  | 0:16 | 0.14 |  |  | Yes
11KV YANLEMO | SE |  |  | 2022-08-05 17:36 | 2.2 |  | due to Mai unguwa 500KVA S/S on fire, | YES | 2022-08-05 21:27 |  | 3:51 | 0.35292 |  |  | Yes
33KV SUMAILA | TL |  |  | 2022-08-05 17:40 |  | E/F | Rungumau isolator opened | NO | 2022-08-05 20:40 |  | 3:00 | 0 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-05 18:49 | 7.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-05 18:55 |  | 0:06 | 0.0325 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-05 19:19 | 9.6 | E/F | Nassarawa leg was isolated | NO | 2022-08-05 20:33 |  | 1:14 | 0.49333 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-05 19:40 | 13 | O/C | TRANSIENT | TRANSIENT | 2022-08-05 19:55 |  | 0:15 | 0.13542 |  |  | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-05 20:13 | 14.9 | O/C | TRANSIENT | TRANSIENT | 2022-08-05 20:38 |  | 0:25 | 0.25868 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-05 20:44 | 14 | E/F | Tree trimming behind Dakata T/S | YES | 2022-08-05 22:45 |  | 2:01 | 1.1764 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-05 21:05 | 0.8 | E/F | Dawakin kudu 300kva 1no. J&P Dropped R phase amened | YES | 2022-08-05 22:04 |  | 0:59 | 0.032778 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-05 21:54 | 3.1 | E/F | 33KV Jahun feeder was tried & stayed after opened Shuwarin and Dantata isolators, RE JGS approved. | NO | 2022-08-06 09:17 |  | 11:23 | 1.4703 |  |  | No
33KV GARKO | TL |  |  | 2022-08-05 22:11 | 2 | E/F | 33KV Garko feeder was tried and stayed after Garko, Darki and Jigaware legs were isolated as suspected faulty segment. RE KNE Hotoro approved. | NO | 2022-08-06 12:28 |  | 14:17 | 1.1903 |  |  | No
33KV MUSAWA | TL |  |  | 2022-08-05 22:27 | 4.1 | E/F | Kasada and Musawa leg opened | NO | 2022-08-06 08:35 |  | 10:08 | 1.7311 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-05 22:31 | 0.5 | E/F | 33KV Bagauda feeder tried and stayed after bat bridged the line at Farida Farm and R-phase touching channel iron at Al-Mokab it was removed at repositioned respectively. RE Dangora approved. | YES | 2022-08-06 09:45 |  | 11:14 | 0.23403 |  |  | No
11KV MAIDUGURI ROAD | TL |  |  | 2022-08-05 23:03 |  | E/F | After rectifying fault on *11KV Maiduguri breaker*. Broken spring charging mechanism replaced. | YES | 2022-08-06 18:30 |  | 19:27 | 0 |  |  | No
33KV LAW SCHOOL | TL |  |  | 2022-08-05 23:06 | 3.2 | E/F | Tarau isolator was opened | NO | 2022-08-06 07:19 |  | 8:13 | 1.0956 |  |  | No
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 6
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV KARAYE | TL |  |  | 2022-08-06 00:30 | 2.1 | E/F | Yelwan faki isolator was opened | NO | 2022-08-06 07:20 |  | 6:50 | 0.59792 |  |  | Yes
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-06 00:39 | 9 | O/C | TRANSIENT | TRANSIENT | 2022-08-06 00:49 |  | 0:10 | 0.0625 |  |  | Yes
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-06 00:49 |  | O/C & E/F | Gwazaye isolator wasw opened | NO | 2022-08-06 06:49 |  | 6:00 | 0 |  |  | Yes
33KV MALUMFASHI | TL |  |  | 2022-08-06 00:35 | 1.8 | E/F |  |  |  |  | -44779.0243 | -80602.2437 |  |  | No
33KV BIRNIN KUDU | TL |  |  | 2022-08-06 01:25 | 2.4 | O/C | TRANSIENT | YES | 2022-08-06 01:35 |  | 0:10 | 0.016667 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-06 01:40 | 3 | O/C & E/F | BUK ISOLATOR WAS OPENED | NO | 2022-08-06 08:20 |  | 6:40 | 0.83333 |  |  | Yes
33KV BIRNIWA | TL |  |  | 2022-08-06 01:30 | 0.7 | E/F | 33KV Birniwa feeder was tried and stayed after Gayin isolator opened. RE JGN approved. | NO | 2022-06-08 09:41 |  | -58.659 | -41.0613 |  |  | No
33KV BIRNIN KUDU | TL |  |  | 2022-08-06 01:55 | 2.2 | O/C & E/F | Danmasara isolator was opened | NO | 2022-08-06 08:32 |  | 6:37 | 0.60653 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-06 03:04 | 2.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-06 03:14 |  | 0:10 | 0.018056 |  |  | #N/A
33KV MAMMAN NASIR | TL |  |  | 2022-08-06 04:36 | 1.2 | E/F | 33kV M/Nasir feeder was tried and stayed with nothing found. RE KTS Malumfashi approved. | NO | 2022-06-08 09:55 |  | -58.7785 | -70.5342 |  |  | No
33KV GUMEL | TL |  |  | 2022-08-06 07:39 | 0.9 | E/F | 33kV Gumel feeder was tried & stayed okay, Kaugama leg was isolated. RE JGS approved. | NO | 2022-06-08 09:23 |  | -58.9278 | -53.035 |  |  | No
33KV KURNA | TL |  |  | 2022-08-06 08:52 | 6 | O/C & E/F | 33KV Kurna feeder after opened Abattoir isolator. RE Dala approved. | NO | 2022-06-08 13:11 |  | -58.8201 | -352.9208 |  |  | No
11KV MAJE | TL |  |  | 2022-06-08 09:26 | 2.3 | O/C & E/F | 11KV Maje feeder tried and stayed after branch of tree removed along the line. TE Hadejia approved. | NO | 2022-06-08 11:35 |  | 2:09 | 0.20604 |  |  | Yes
33KV BUK | TL |  |  | 2022-06-08 09:45 |  | O/C & E/F | 33KV BUK feeder was tried and stayed after opened isolator at Kofar Famfo. RE KNN Kabuga approved. | NO | 2022-06-08 11:38 |  | 1:53 | 0 |  |  | Yes
33KV CLUB | PM | 2022-06-08 10:00 | 2022-06-08 15:00 | 2022-06-08 10:07 | 6.5 |  | to carryout tree trimming along the line. |  | 2022-06-08 15:06 |  | 4:59 | 1.3497 | Yes
11KV AMINU KANO | PM | 2022-06-08 10:00 | 2022-06-08 13:00 | 2022-06-08 10:08 |  |  | to enable KEDCO contractor Mr Idris Muhammad Aminu Yakasai LTD effect correctional observations by NEMSA @300KVA 11/0.415 S/S MET West Steel Kofar Dawanau Kano. |  | 2022-06-08 12:31 |  | 2:23 | 0 | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-06-08 09:51 | 2.8 | E/F | 33kV B/Kudu feeder tried and stayed after line element cut off at Gaudi Ruru it was replaced also Dan Masara Isolator is in open position. RE JGS approved. | NO | 2022-06-08 10:45 |  | 0:54 | 0.105 |  |  | Yes
33KV NNPC | PM | 2022-06-08 10:00 | 2022-06-08 10:30 | 2022-06-08 10:08 | 10.9 |  | to enable KEDCO contractor Mr Idris Muhammad Aminu Yakasai LTD effect correctional observations by NEMSA @300KVA 11/0.415 S/S MET West Steel Kofar Dawanau Kano. |  | 2022-06-08 10:32 |  | 0:24 | 0.18167 | Yes
33KV CBN | PM | 2022-06-08 10:00 | 2022-06-08 10:30 | 2022-06-08 10:15 | 5.8 |  | to open Dangi flyover isolated to enable Kano Industrial Region Crew from Zoo Road TSP to eliminate the flash point between Ajasa and Dr. Bala feeders at Iyaka Road opposite Audu Bako secretariat. |  | 2022-06-08 10:49 |  | 0:34 | 0.13694 | No | 0:04
11KV DR BALA | PM | 2022-06-08 10:00 | 2022-06-08 15:00 | 2022-06-08 10:13 | 0.7 |  | to eliminate flash point at Iyaka Road by Ibrahim Dabo Road and to retension sagged HT LINE AT Audu Bako Secretariat |  | 2022-06-08 14:34 |  | 4:21 | 0.12688 | Yes
11KV KARKASARA | PM | 2022-06-08 10:00 | 2022-06-08 12:00 | 2022-06-08 10:10 | 5.2 |  | to enable us replace HT wooden pole along Rehan Street Tudun Fulani closed to Engr. Hussain Resident. |  | 2022-06-08 14:28 |  | 4:18 | 0.93167 | No | 2:18
11KV INDEPENDENCE | PM | 2022-06-08 10:00 | 2022-06-08 14:00 | 2022-06-08 11:15 |  |  | to KEDCO contractor to allow Matrix International Nig LTD to relocate KEDCO facilities at no 452 Gawuna by Club road. |  | 2022-06-08 15:22 |  | 4:07 | 0 | No | 0:07
11KV AHMADU BELLO | PM | 2022-06-08 10:00 | 2022-06-08 18:00 | 2022-06-08 11:42 |  |  | to enable carryout tree trimming along the line. |  | 2022-06-08 18:51 |  | 7:09 | 0 | Yes
33KV SULE LAMIDO UNIVERSITY | TL |  |  | 2022-06-08 10:45 | 0.1 | E/F | 33KV University feeder was tried and stayed after opened isolator at Gidan Sugar. RE JGN approved. | NO | 2022-06-08 13:46 |  | 3:01 | 0.012569 |  |  | #N/A
11KV BANK ROAD | TL |  |  | 2022-06-08 11:08 | 3 | E/F | After Dr. Alkali Isolator was Opened | NO | 2022-08-07 11:42 |  | 1440:34 | 180.0708 |  |  | No
11KV AJASA | PM | 2022-06-08 10:00 | 2022-06-08 14:00 | 2022-06-08 10:00 | 2.4 |  | to enable him Eliminate flash point between 11kV Ajasa and 11kV dr Bala feeders at Zaria Road by Audu Bako secretariat Kano. |  | 2022-06-08 13:10 |  | 3:10 | 0.31667 | Yes
33KV BIRNIW | TL |  |  | 2022-06-08 11:05 | 0.8 | E/F | TASHEGUWA AND GARIN MAGAJI LEGS OPENED | NO | 2022-06-08 16:22 |  | 5:17 | 0.17611 |  |  | #N/A
33KV KAFIN HAUSA | TL |  |  | 2022-06-08 11:18 | 2.5 | E/F | 33KV Hausa feeder tried and stayed after Ganuwar Kuka isolator was opened. RE JGN approved. | NO | 2022-06-08 01:31 |  | -0.40764 | -1.0191 |  |  | No
33KV GASKIYA | TL |  |  | 2022-06-08 12:07 | 11 | E/F | 33KV Gaskiya feeder tried and stayed after Nassarawa isulator opened as suspected segment. RE KNE Kawaji approved. | YES | 2022-06-08 13:31 |  | 1:24 | 0.64167 |  |  | Yes
33KV KOFAR GUGA | TL |  |  | 2022-06-08 12:33 | 4.5 | E/F | 33KV Kofar Guga tried and stayed after bird bridged the line at Orthopedic Katsina. RE KTN approved. | YES | 2022-06-08 14:15 |  | 1:42 | 0.31875 |  |  | Yes
33KV GANO | TL |  |  | 2022-06-08 12:57 | 1 | E/F | 33KV Gano feeder tried and stayed after blow 3no fused at Daurawar Naabba T-off. RE KNE Hotoro approved. | YES | 2022-06-08 14:28 |  | 1:31 | 0.063194 |  |  | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-06-08 11:31 | 1 | E/F | 33kV B/Kudu feeder tried and stayed after Dan Masara Isolator was opened. RE JGS approved. | NO | 2022-06-08 13:36 |  | 2:05 | 0.086806 |  |  | Yes
33KV SUMAILA | TL |  |  | 2022-06-08 12:41 | 2.4 | O/C & E/F | After opened Ringumau isolator as suspected faulty segment. | NO | 2022-08-06 23:57 |  | 1427:16 | 142.7267 |  |  | No
33KV JAHUN | TL |  |  | 2022-06-08 12:41 | 3.5 | E/F | After Shuwarin Isolator was Opened | NO | 2022-08-07 06:35 |  | 1433:54 | 209.1104 |  |  | No
33KV KWANKWASO | TL |  |  | 2022-06-08 13:00 | 4.9 | E/F | KAFIN AGUR ISOLATOR OPENED | NO | 2022-06-08 16:19 |  | 3:19 | 0.67715 |  |  | Yes
11KV MAI RUWA | TL |  |  | 2022-06-08 15:55 | 0.6 | E/F | 11KV Mai Ruwa feeder tried and stayed after replaced broken disc insulator R-phase at Barabari T-off. TE KT Road approved. | YES | 2022-07-08 18:35 |  | 722:40 | 18.0667 |  |  | No
33KV RIJIYAR ZAKI | TL |  |  | 2022-06-08 14:18 | 15.5 | E/F | HAWAN DAWAKI ISOLATOR | NO | 2022-06-08 16:15 |  | 1:57 | 1.2594 |  |  | Yes
11KV N.N.D.C. | SE |  |  | 2022-06-08 14:02 | 3.6 |  | 11KV NNDC feeder was opened on emergency due to vehicle hit LT pole at Yahaya Gusau Road, NNDC link 3. Reported by TE Sharada TSP. Faulty portion was isolated. |  | 2022-06-08 15:35 |  | 1:33 | 0.2325 |  |  | #N/A
11KV FARAWA | TL |  |  | 2022-06-08 16:23 |  | O/C & E/F | After opened Zara isolator as suspected faulty segment. | NO | 2022-08-06 20:44 |  | 1420:21 | 0 |  |  | No
33KV KURNA | TL |  |  | 2022-08-06 16:55 | 1.8 | O/C & E/F | After opened an isolator at Abattoir as suspected faulty segment. | YES | 2022-08-06 17:58 |  | 1:03 | 0.07875 |  |  | Yes
33KV GANO | SE |  |  | 2022-08-06 17:34 | 4.8 |  | After opened an isolator at *Dorowar Na - abba* due to burnt Yellow & Blue phases male contact. | YES | 2022-08-06 18:26 |  | 0:52 | 0.17333 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-06 17:52 | 14 | O/C | NOTHING FOUND | NO | 2022-08-06 17:57 |  | 0:05 | 0.048611 |  |  | Yes
33KV MUSAWA | TL |  |  | 2022-08-06 19:27 | 4.7 | [5 empty] | -44779.8104 | -210465.109 |  |  | No
33KV FALGORE | TL |  |  | 2022-08-06 17:37 | 3.2 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-06 21:03 |  | 3:26 | 0.45778 |  |  | Yes
33KV KARAYE | TL |  |  | 2022-08-06 21:02 | 3 | O/C | After opened an isolator at Dangora as suspected faulty segment. | NO | 2022-08-06 23:16 |  | 2:14 | 0.27917 |  |  | Yes
33KV GAYA | TL |  |  | 2022-08-06 21:30 | 1.7 | E/F | After opened KUT isolator as suspected faulty segment. | NO | 2022-08-07 05:40 |  | 8:10 | 0.57847 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-06 21:24 | 1.3 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-06 21:24 |  | 0:00 | 0 |  |  | No
11KV ZAWACIKI | TL |  |  | 2022-08-06 21:08 | 3.8 | O/C | NOTHING FOUND | TRANSIENT | 2022-08-06 21:28 |  | 0:20 | 0.052778 |  |  | Yes
11KV TUDUN WADA | TL |  |  | 2022-08-06 21:40 |  | O/C | NOTHING FOUND | TRANSIENT | 2022-08-06 23:25 |  | 1:45 | 0 |  |  | Yes
33KV BUK | TL |  |  | 2022-08-06 23:34 |  | O/C | After Kofar Famfo isolator was opened. | NO | 6691463.0507 |  | 6646683.0687 | 0 |  |  | No
11KV MURTALA MOHD | TL |  |  | 2022-08-07 23:44 |  | O/C | NOTHING FOUND | NO | 2022-08-07 07:05 |  | -0.69375 | 0 |  |  | #N/A
33KV BAGAUDA | TL |  |  | 2022-08-06 23:49 | 4.7 | E/F | After opened Tamburawa isolator as suspected faulty segment. | NO | 2022-08-07 08:43 |  | 8:54 | 1.7429 |  |  | No
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 7
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV FALGORE | TL |  |  | 2022-08-07 00:20 | 2.6 | E/F | After Tudun Wada leg isolated as suspected faulty segment | NO | 2022-08-07 07:10 |  | 6:50 | 0.74028 |  |  | Yes
33KV SULE LAMIDO UNIVERSITY | TL |  |  | 2022-08-07 00:27 | 0.1 | E/F | Opened Gidan Sugar isolato | NO | 2022-08-07 09:22 |  | 8:55 | 0.037153 |  |  | #N/A
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-07 00:34 | 3.2 | O/C | NOTHING FOUND | NO | 2022-08-07 00:40 |  | 0:06 | 0.013333 |  |  | #N/A
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-07 00:57 | 3.2 | E/F | After 33kv Dr. Jamil Isolated | NO | 2022-08-07 01:01 |  | 0:04 | 0.0088889 |  |  | #N/A
33KV DUTSE | TL |  |  | 2022-08-07 01:11 | 4.8 | O/C | Nothing found | NO | 2022-08-07 01:48 |  | 0:37 | 0.12333 |  |  | Yes
33KV WATARI | TL |  |  | 2022-08-07 01:22 | 0.1 | E/F |  |  |  |  | -44780.0569 | -4478.0057 |  |  | No
33KV GEZAWA | TL |  |  | 2022-08-07 01:31 |  | O/C & E/F | After opened an isolator at Zauran Danbaba as suspected faulty segment. | NO | 2022-08-07 08:06 |  | 6:35 | 0 |  |  | Yes
33KV MASHI | TL |  |  | 2022-08-07 01:50 | 2.2 | O/C | Isolated Sharuwa T-off due to Y-phase fuse line element cut, | YES | 2022-08-07 16:57 |  | 15:07 | 1.3857 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-07 02:44 | 2.2 | O/C | Transinet | NO | 2022-08-07 05:54 |  | 3:10 | 0.29028 |  |  | #N/A
33KV TEXTILE | TL |  |  | 2022-08-07 03:09 | 2.9 | E/F | Removed a Owl that bridged the line @ U/Fulani | YES | 2022-08-07 09:54 |  | 6:45 | 0.81562 |  |  | No
33KV MAMMAN NASIR | TL |  |  | 2022-08-07 03:00 | 1.7 | E/F |  |  |  |  | -44780.125 | -76126.2125 |  |  | No
33KV LAW SCHOOL | TL |  |  | 2022-08-07 04:48 | 2.5 | O/C | Nothing found | NO | 2022-08-07 04:55 |  | 0:07 | 0.012153 |  |  | Yes
33KV DUTSE | TL |  |  | 2022-08-07 05:34 | 4.7 | E/F | After tree trimming was conducted at Jada | YES | 2022-08-07 08:53 |  | 3:19 | 0.64951 |  |  | Yes
33KV BIRNIWA | TL |  |  | 2022-08-07 06:06 | 0.5 | E/F | 33KV Birniwa feeder tried and stayed after R-phase J&P amended at Kudit 200KVA S/S. RE JGN approved. | YES | 2022-08-07 21:49 |  | 15:43 | 0.32743 |  |  | No
33KV GARKO | TL |  |  | 2022-08-07 08:44 | 1.3 | E/F | Removed a Bird that bridged the line Tudun Ginsau, | YES | 2022-08-07 13:32 |  | 4:48 | 0.26 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-07 09:38 | 12 | O/C & E/F | OPENED JOGANA ISOLATOR | NO | 2022-08-07 10:40 |  | 1:02 | 0.51667 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-07 10:09 | 3 | O/C & E/F | OPENED ZAURAN DAN BABA | NO | 2022-08-07 12:26 |  | 2:17 | 0.28542 |  |  | Yes
11KV HOUSING ESTATE | PM | 2022-08-07 10:00 | 2022-08-07 12:00 | 2022-08-07 10:10 | 3.3 |  | For safe working space to enable Kedco contractor Bok Engineering to change source for Alh. Abubakar Lawan 50KVA S/S from H/Estate 11kV fdr to Dala Foods 11kV fdr |  | 2022-08-07 11:10 |  | 1:00 | 0.1375 | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-07 10:13 | 2.5 | O/C & E/F | OPENED DR JAMIL FDR | NO | 2022-08-07 10:50 |  | 0:37 | 0.064236 |  |  | #N/A
33KV RIJIYAR ZAKI | PM | 2022-08-07 10:00 | 2022-08-07 13:00 | 2022-08-07 10:20 | 13.7 |  | To enable Kedco contractor Al-Ihsan Engineering relocate HT poles @ Sani Abacha Youth Centre Madobi Road |  | 2022-08-07 18:45 |  | 8:25 | 4.8045 | No | 5:25
33KV GASKIYA | PM | 2022-08-07 10:00 | 2022-08-07 18:00 | 2022-08-07 10:22 | 12 |  | To enable KEDCO Contractor SANROUK Engineering services continue with rehabilitation work along the line under Capex project, |  | 2022-08-07 16:28 |  | 6:06 | 3.05 | Yes
33KV BAGAUDA | PM | 2022-08-07 10:00 | 2022-08-07 16:00 | 2022-08-07 10:30 | 1 |  | For safe working space to enable Kedco contractor Digibit Control install 1.5MVA 33/11kV & 1.0MVA 11/0.415kV Transformers @ Asin Integrated Farms LTD |  | 2022-08-07 16:42 |  | 6:12 | 0.25833 | No | 0:12
33KV NNPC | PM | 2022-08-07 10:00 | 2022-08-07 10:30 | 2022-08-07 11:00 |  |  |  |  | 2022-08-07 11:30 |  | 0:30 | 0 | Yes
33KV ZARIA ROAD | PM | 2022-08-07 11:30 | 2022-08-07 14:30 | 2022-08-07 11:45 |  |  | To effect corrections/observations by Nemsa on Sahaibco InternationalShopping Complex Karkasara kano, |  | 2022-08-07 14:20 |  | 2:35 | 0 | Yes
33KV DR. JAMIL GWAMNA | PM | 2022-08-07 10:00 | 2022-08-07 16:00 | 2022-08-07 12:00 | 1 |  | To enable Kedco contractor Digibit Control install 1.5MVA 33/11kV & 1.0MVA 11/0.415kV Transformers @ Asin Integrated Farms LTD |  | 2022-08-07 15:18 |  | 3:18 | 0.1375 | Yes
33KV SPANISH 2 | TL |  |  | 2022-08-07 12:15 | 24 | O/C | TRANSIENT | TRANSIENT | 2022-08-07 12:25 |  | 0:10 | 0.16667 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-07 12:32 | 2.8 | O/C & E/F | OPENED ZANGO ISOLATOR | NO | 2022-08-07 15:55 |  | 3:23 | 0.39472 |  |  | Yes
11KN KANTI | PM | 2022-08-07 11:00 | 2022-08-07 15:00 | 2022-08-07 12:45 |  |  | To enable Kedco contractor Khaleesha Electrical install 100KVA Transformer @A.A Rano filling station Kazaure |  | 2022-08-07 18:02 |  | 5:17 | 0 | No | 1:17
33KV SPANISH 2 | TL |  |  | 2022-08-07 12:46 | 14 | E/F | NOTHING FOUND | NO | 2022-08-07 15:42 |  | 2:56 | 1.7111 |  |  | Yes
11KV DALA FOODS | PM | 2022-08-07 13:00 | 2022-08-07 15:00 | 2022-08-07 13:00 |  |  | For safe working space to enable Kedco contractor Bok Engineering install Alh. Abubakar Lawan 50KVA S/S along Sharada Road, |  | 2022-08-07 14:50 |  | 1:50 | 0 | Yes
33KV KAITA | TL |  |  | 2022-08-07 13:40 | 5.5 | E/F | Opened High Court and Kaita leg, | NO | 2022-08-07 14:42 |  | 1:02 | 0.23681 |  |  | Yes
33KV SUMAILA | TL |  |  | 2022-08-07 13:43 | 2.1 | E/F |  |  |  |  | -44780.5715 | -94039.2002 |  |  | No
33KV BUK | TL |  |  | 2022-08-07 14:09 | 22 | O/C | TRANSIEN | TRANSIENT | 2022-08-07 14:22 |  | 0:13 | 0.19861 |  |  | Yes
11KV BANK ROAD | TL |  |  | 2022-08-07 14:20 | 3 | O/C | TRANSIEN | TRANSIENT | 2022-08-07 14:35 |  | 0:15 | 0.03125 |  |  | Yes
33KV JODA | TL |  |  | 2022-08-07 15:46 | 0.1 | E/F | OPENED DANJA ISOLATOR | NO | 2022-08-07 17:33 |  | 1:47 | 0.0074306 |  |  | Yes
11KV MAI RUWA | TL |  |  | 2022-08-07 15:55 | 0.6 | E/F | SHATTERED Y P DISC INSULATOR REPLACED AT BAREBARE /UNGUWAN HAMIDA T-OFF | YES | 2022-08-07 18:35 |  | 2:40 | 0.066667 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-07 16:16 | 5.3 | O/C | TRANSIEN | TRANSIEN | 2022-08-07 16:21 |  | 0:05 | 0.018403 |  |  | Yes
11KV MAIDUGURI ROAD | TL |  |  | 2022-08-07 16:16 | 3.4 | O/C | 11KV Maiduguri feeder tried and stayed after opened Yandodo isolator as suspected faulty segment. TE Hotoro approved. | NO | 2022-08-07 18:15 |  | 1:59 | 0.28097 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-07 16:25 | 3.2 | O/C & E/F | ZAURAN DANBABA OPENED | NO | 2022-08-08 01:30 |  | 9:05 | 1.2111 |  |  | No
11KV TARAUNI | SE |  |  | 2022-08-07 05:18 | 2.9 |  | Due to Bashir Kazaure 200KVA S/S observed smoking, WAS restored back after isolated Bashir Kazaure 200KVA S/S due to R-phase punctured XLPE cable. TE Hotoro approved. | YES | 2022-08-07 18:12 |  | 12:54 | 1.5587 |  |  | No
11KV KABUGA | TL |  |  | 2022-08-07 18:55 |  | O/C & E/F | 11kV Kabuga feeder was restored after amended loose B Phase XLPE Cable touching the Body of Transformer at Habibu Sadik 500kVA S/S. TE R/Zaki certified. | YES | 2022-08-08 02:55 |  | 8:00 | 0 |  |  | No
33KV ZARIA ROAD | TL |  |  | 2022-08-07 18:35 | 15.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-07 18:45 |  | 0:10 | 0.10972 |  |  | Yes
11KV GWARZO ROAD | TL |  |  | 2022-08-07 18:55 |  | O/C & E/F | 11kV Gwarzo Road feeder was tried and stayed after removed a branch of tree at Gwarzo Road opposite Motor Park. TE R/Zaki approved. | YES | 2022-08-08 02:10 |  | 7:15 | 0 |  |  | No
11KV BADAWA | TL |  |  | 2022-08-07 18:20 | 3.2 |  | 11KV Badawa feeder opened on emergency with 3.2MW due to LT pole broken at Garba Link. Faulty portion was isolated. TE Badawa approved. | YES | 2022-08-07 20:46 |  | 2:26 | 0.32444 |  |  | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-07 18:54 | 15.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-07 20:30 |  | 1:36 | 1.04 |  |  | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-07 21:09 | 7.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-07 21:19 |  | 0:10 | 0.052778 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-07 20:36 | 3.1 | E/F |  |  |  |  | -44780.8583 | -138820.6608 |  |  | No
33KV SUMAILA | TL |  |  | 2022-08-07 20:36 |  | E/F | RUNGUMAU OPENED | NO | 2022-08-07 21:34 |  | 0:58 | 0 |  |  | Yes
11KV MAIDUGURI ROAD | TL |  |  | 2022-08-07 21:28 | 1.4 | NO RI | 11KV Maiduguri feeder tried and stayed after opened Yandodo isolator as suspected faulty segment. TE Hotoro approved. | NO | 2022-08-07 22:45 |  | 1:17 | 0.074861 |  |  | Yes
33KV GAYA | TL |  |  | 2022-08-07 21:20 | 1.4 | E/F | TREE TRIMMING WAS CONDUCTED ALONG THE LINE | NO | 2022-08-09 09:52 |  | 36:32 | 2.1311 |  |  | No
33KV WUDIL | TL |  |  | 2022-08-07 21:20 | 2.5 | O/C | ISOLATED 33KV GAYA FOR LINE PaTROL | YES | 2022-08-07 21:26 |  | 0:06 | 0.010417 |  |  | Yes
11KV AHMADU BELLO | TL |  |  | 2022-08-07 21:43 | 2.8 | E/F | 11KV Ahmadu Bello feeder tried and stayed after isolator at Dawaki road as suspected faulty segment. TE HQ TSP approved. | NO | 2022-08-07 22:57 |  | 1:14 | 0.14389 |  |  | Yes
33KV GARKO | TL |  |  | 2022-08-07 22:06 | 1.3 | E/F | OPENED JIGAWARE, GARKO AND DARKI LEGS | NO | 2022-08-07 12:44 |  | -0.39028 | -0.50736 |  |  | No
33KV COCA COLA | TL |  |  | 2022-08-07 22:37 | 7.2 | O/C & E/F | PROSPER JUNCTION OPENED | NO | 2022-08-08 00:40 |  | 2:03 | 0.615 |  |  | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-08-07 22:56 | 4.2 | E/F | OPENED DANMASARA ISOLATOR | NO | 2022-08-08 09:07 |  | 10:11 | 1.7821 |  |  | No
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 8
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV BAGAUDA | TL |  |  | 2022-08-08 00:08 | 2.4 | E/F | 33KV Bagauda feeder was tried and stayed after opened Tamburawa Isolator, RE Dangora approved. | YES | 2022-08-08 07:31 |  | 7:23 | 0.73833 |  |  | No
33KV BIRNIWA | TL |  |  | 2022-08-08 00:43 | 0.3 | E/F | opened garin magaji leg | NO | 2022-08-08 11:57 |  | 11:14 | 0.14042 |  |  | No
33KV GUMEL | TL |  |  | 2022-08-08 00:48 | 0.9 | E/F | REPOSITIONED PULLED OUT R&B PHASES CONDUCTORS BEHIND HADEJIA TS | YES | 2022-08-08 13:14 |  | 12:26 | 0.46625 |  |  | No
33KV KAFIN HAUSA | TL |  |  | 2022-08-08 00:55 | 2.2 | E/F | OPENED AUYO LEG | NO | 2022-08-08 10:41 |  | 9:46 | 0.89528 |  |  | No
33KV HADEJIA | TL |  |  | 2022-08-08 00:59 | 3.3 | E/F | 11kV Kabuga feeder was opened on Emergency with 3.5MW, due to Abnormal Sound Heard from Habibu Sadik 500kVA S/S. TE Dorayi reported. OPENED GIDAN LEDA ISOLATOR | NO | 2022-08-08 08:52 |  | 7:53 | 1.084 |  |  | No
11KV KABUGA | TL |  |  | 2022-08-08 00:58 | 3.5 | [5 empty] | -44781.0403 | -156733.641 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-08 02:43 | 1.9 | O/C & E/F | ISOLATED 33KV DR JAMIL FEDDER FOR LINE PATROL |  | 2022-08-08 03:08 |  | 0:25 | 0.032986 |  |  | #N/A
33KV DR. JAMIL GWAMNA | TL |  |  | 2022-08-08 02:43 | 1.9 |  | NOTHING FOUND |  | 2022-08-08 03:30 |  | 0:47 | 0.062014 |  |  | #N/A
33KV KWANKWASO | TL |  |  | 2022-08-08 02:49 | 3.8 | O/C & E/F | OPENED KAFIN AGUR ISOLATOR | NO | 2022-08-08 10:33 |  | 7:44 | 1.2244 |  |  | Yes
11KV MAKAMA | TL |  |  | 2022-08-08 03:16 | 1.1 | O/C & E/F | amended r- PHASE J&P AT BABALLE JAJI 500KVA S/S | NO | 2022-08-08 12:05 |  | 8:49 | 0.4041 |  |  | No
33KV WUDIL | TL |  |  | 2022-08-08 03:16 | 1.8 | O/C | REPOSITIONED PULLED OUT Y- PHASE CONDUCTOR AT WUDIL GENERAL HOSPITAL. | YES | 2022-08-08 10:20 |  | 7:04 | 0.53 |  |  | No
33KV GANO | TL |  |  | 2022-08-08 03:20 | 5.1 | E/F | OPENED POLAC ISOLATOR | NO | 2022-08-08 10:50 |  | 7:30 | 1.5938 |  |  | No
33KV GASKIYA | TL |  |  | 2022-08-08 03:31 | 10 | O/C |  |  |  |  | -44781.1465 | -447811.4653 |  |  | No
33KV FLOUR MILLS | TL |  |  | 2022-08-08 03:33 | 15 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 03:43 |  | 0:10 | 0.10417 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-08 03:33 | 8 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 06:56 |  | 3:23 | 1.1278 |  |  | Yes
33KV SMALL SCALE | TL |  |  | 2022-08-08 03:53 | 2.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 05:35 |  | 1:42 | 0.17708 |  |  | Yes
33KV IDH | TL |  |  | 2022-08-08 03:56 | 7 | O/C | AMENDED CUT R- PHASE CONDUCTOR AT NEW ROAD BY MOTOR PARK. | NO | 2022-08-08 14:55 |  | 10:59 | 3.2035 |  |  | No
11KV RIMIN KEBE | TL |  |  | 2022-08-08 03:35 | 2.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 05:47 |  | 2:12 | 0.23833 |  |  | Yes
11KV AIRPORT ROAD | TL |  |  | 2022-08-08 03:40 | 1.2 | O/C & E/F | NOTHING FOUND | NO | 2022-08-08 15:05 |  | 11:25 | 0.57083 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-08 03:45 | 1.9 | O/C & E/F | TAMBURAWA ISOLATOR WAS OPENED | NO | 2022-08-08 07:40 |  | 3:55 | 0.31007 |  |  | #N/A
11KV HOTORO | TL |  |  | 2022-08-08 03:46 | 3 | O/C & E/F | AMENDED B- PHASE J&P AT SANI MASHAL 200KVA S/S | YES | 2022-08-08 09:17 |  | 5:31 | 0.68958 |  |  | No
33KV ZARIA ROAD | TL |  |  | 2022-08-08 03:46 | 16.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 07:02 |  | 3:16 | 2.2594 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-08 03:47 | 5.6 | O/C | 33KV CBN feeder was tried and stayed after opened Halliru Akilu isolator. RE KNC Nass. approved. | YES | 2022-08-08 08:40 |  | 4:53 | 1.1394 |  |  | Yes
11KV BADAWA | TL |  |  | 2022-08-08 03:40 | 2.7 | O/C | SS1 300KVA S/S ISOLATED ITSELF | NO | 2022-08-08 12:20 |  | 8:40 | 0.975 |  |  | No
11KV AHMADU BELLO | TL |  |  | 2022-08-08 03:42 | 2.5 | O/C | OPENED DAWAKI ROAD ISOLATOR | NO | 2022-08-08 04:46 |  | 1:04 | 0.11111 |  |  | Yes
11KV AUDO BAKO | TL |  |  | 2022-08-08 03:43 | 1.5 | O/C | NOTHING FOUND | NO | 2022-08-08 14:10 |  | 10:27 | 0.65313 |  |  | #N/A
11KV FANISAU | TL |  |  | 2022-08-08 03:50 | 2 | E/F | OPENED UNGOGO ISOLATOR | NO | 2022-08-08 15:04 |  | 11:14 | 0.93611 |  |  | No
11KV TUKUNTAWA | TL |  |  | 2022-08-08 03:50 | 2 | O/C | NOTHING FOUND | NO | 2022-08-08 08:51 |  | 5:01 | 0.41806 |  |  | No
11KV SAGAGI | TL |  |  | 2022-08-08 03:52 | 2.5 | O/C | Amended Y-phase J&P @ Major Hadi relief 300KVA S/S, | YES | 2022-08-08 18:09 |  | 14:17 | 1.4878 |  |  | No
11KV HOUSING ESTATE | TL |  |  | 2022-08-08 03:52 | 2.2 | O/C | NOTHING FOUND | YES | 2022-08-08 08:15 |  | 4:23 | 0.40181 |  |  | No
11KV ORTHOPAEDIC | TL |  |  | 2022-08-08 03:53 | 1.7 | O/C | AMENDED B- PHASE J&P AT MOTAR SOJA 500KVA S/S | YES | 2022-08-08 14:05 |  | 10:12 | 0.7225 |  |  | No
11KV FEDERAL SECRETARIAT | TL |  |  | 2022-08-08 03:53 | 2.5 | O/C | CONDUCTED TREE TRIMMING ATGGC DALA AND ISOLATED KABARIN WALI 500KVA S/S DUE TO 2NO. J&P DROPPED. | NO | 2022-08-08 15:05 |  | 11:12 | 1.1667 |  |  | No
11KV BACHIRAWA | TL |  |  | 2022-08-08 03:52 | 2.5 | O/C | Amended R-phase J&P @ R/Lemo Kuto 500KVA S/S, | YES | 2022-08-08 18:01 |  | 14:09 | 1.474 |  |  | No
33KV KURNA | TL |  |  | 2022-08-08 03:56 | 10.5 | O/C & E/F | OPENED ABATTOIR ISOLATOR | NO | 2022-08-08 10:34 |  | 6:38 | 2.9021 |  |  | No
11KV RACE COURSE | TL |  |  | 2022-08-08 03:57 | 1.5 | O/C | REMOVED BRANCH OF TREE ON THE LINE AT MAKAMA. | NO | 2022-08-08 14:05 |  | 10:08 | 0.63333 |  |  | No
11KV BANK ROAD | TL |  |  | 2022-08-08 03:58 | 2 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 06:40 |  | 2:42 | 0.225 |  |  | Yes
11KV KOFAR NA'ISA | TL |  |  | 2022-08-08 03:50 | 2.9 | O/C | NOTHING FOUND | NO | 2022-08-08 10:15 |  | 6:25 | 0.77535 |  |  | #N/A
33KV DANGOTE | TL |  |  | 2022-08-08 03:52 | 6 | O/C | 33KV Dangote feeder was tried and stayed after opened AA Rano and Kwanar Ganduje isolators as suspected faulty segment . RE KNI Sharada approved. | NO | 2022-08-08 08:00 |  | 4:08 | 1.0333 |  |  | Yes
11KV SHARADA INDUSTRIAL | TL |  |  | 2022-08-08 03:53 | 1.9 | O/C | AMENDED B- PHASE J&P AT RAIRAYIN ISA RELIEF 300KVA S/S | YES | 2022-08-08 10:30 |  | 6:37 | 0.52382 |  |  | No
11KV CITY | TL |  |  | 2022-08-08 03:52 | 1.9 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 04:53 |  | 1:01 | 0.080486 |  |  | Yes
11KV IBRAHIM TAIWO | TL |  |  | 2022-08-08 03:52 | 1.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 04:53 |  | 1:01 | 0.063542 |  |  | Yes
11KV KOFAR NASSARAWA | TL |  |  | 2022-08-08 03:52 | 2.1 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 04:53 |  | 1:01 | 0.088958 |  |  | Yes
11KV DALA FOODS | TL |  |  | 2022-08-08 03:50 | 2 | O/C | NOTHING FOUND | NO | 2022-08-08 10:50 |  | 7:00 | 0.58333 |  |  | No
33KV ATM | TL |  |  | 2022-08-08 03:52 | 2.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 06:48 |  | 2:56 | 0.30556 |  |  | Yes
11KV N.N.D.C. | TL |  |  | 2022-08-08 03:54 | 2 | E/F | NOTHING FOUND | NO | 2022-08-08 13:10 |  | 9:16 | 0.77222 |  |  | #N/A
11KV JAKARA | TL |  |  | 2022-08-08 03:55 | 1.9 | E/F | REPOSITIONED B- PHASE CONDUCTOR RESTING ON CONCRETE POLE AT DUBAI MARKET | NO | 2022-08-08 12:51 |  | 8:56 | 0.70722 |  |  | No
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-08 03:55 | 9.5 | E/F | A11 ISOLATOR WAS OPENED | YES | 2022-08-08 07:58 |  | 4:03 | 1.6031 |  |  | Yes
11KV CHIRANCI | TL |  |  | 2022-08-08 03:55 | 3 | E/F |  |  |  |  | -44781.1632 | -134343.4896 |  |  | No
33KV BUK | TL |  |  | 2022-08-08 03:55 | 15.3 | E/F | 33KV BUK feeder was tried and stayed after Kofar Famfo isolator was opened. RE KNN Kabuga axis approved. | YES | 2022-08-08 08:41 |  | 4:46 | 3.0387 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-08 03:56 | 2.6 | E/F | Law School 33KV fdr was tried and stayed after opened Tarau isolator, RE Dangora approved. | NO | 2022-08-08 07:19 |  | 3:23 | 0.36653 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-08 04:01 | 10 | O/C | AMENDED Y- PHASE J&P AT AM PLASTIC 500KVA S/S | YES | 2022-08-08 09:14 |  | 5:13 | 2.1736 |  |  | Yes
11KV JAEN | TL |  |  | 2022-08-08 04:02 | 2.7 | O/C | amended r- phase j&p at jaen makera 500kva s/s | NO | 2022-08-08 12:05 |  | 8:03 | 0.90562 |  |  | No
33KV SPANISH 2 | TL |  |  | 2022-08-08 04:02 | 14 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 07:19 |  | 3:17 | 1.9153 |  |  | Yes
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-08 04:04 | 3.4 | O/C |  |  |  |  | -44781.1694 | -152255.9761 |  |  | #N/A
33KV ANGELS | TL |  |  | 2022-08-08 04:14 | 8.4 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 06:48 |  | 2:34 | 0.89833 |  |  | Yes
33KV FALGORE | TL |  |  | 2022-08-08 04:34 | 0.19028 | E/F | - 33KV Falgore feeder was tried and stayed after Gidan Kwano Isolator opened as suspected faulty segment. RE KNW Dangora approved. | YES | 2022-08-08 07:20 |  | 2:46 | 0.021935 |  |  | Yes
33KV MASHI | TL |  |  | 2022-08-08 00:55 | 1.9 | O/C | OPENED GODAI LEG | NO | 2022-08-08 09:59 |  | 9:04 | 0.71778 |  |  | No
33KV MAMMAN NASIR | TL |  |  | 2022-08-08 01:29 | 0.061806 | E/F | CONDUCTED TREE TRIMMING AT WANZAMAI | YES | 2022-08-08 10:57 |  | 9:28 | 0.024379 |  |  | No
33KV JAHUN | TL |  |  | 2022-08-08 02:23 | 0.5 | E/F | REPOSITIONED B- PHASE CONDUCTOR RESTING ON CONCRETE POLE AT AJAWA | YES | 2022-08-08 13:33 |  | 11:10 | 0.23264 |  |  | No
11KV DAURAMA | TL |  |  | 2022-08-08 04:53 | 2 | E/F | 11KV Daurama feeder tried and stayed after branch of tree removed at Dumurkol village. TE Daura approved | YES | 2022-08-08 07:07 |  | 2:14 | 0.18611 |  |  | Yes
11KV AJASA | TL |  |  | 2022-08-08 05:57 | 2.1 | E/F | OPENED JUMPER AT GIDAN MALAMAI AFFECTING 9NO. S/S | NO | 2022-08-08 15:05 |  | 9:08 | 0.79917 |  |  | No
33KV MAI ADUA | TL |  |  | 2022-08-08 06:05 | 2.4 | O/C |  |  |  |  | -44781.2535 | -107475.0083 |  |  | No
11KV KAURA GOJE | TL |  |  | 2022-08-08 03:55 | 1 | O/C | NOTHING FOUND | NO | 2022-08-08 15:05 |  | 11:10 | 0.46528 |  |  | No
11KV BANK ROAD | TL |  |  | 2022-08-08 06:45 | 1.5 | O/C | @0804hrs11KV Bank Road feeder tried and stayed after amended 1no J&P at Agric 500KV. TE HQ approved. | YES | 2022-08-08 08:04 |  | 1:19 | 0.082292 |  |  | Yes
33KV JODA | TL |  |  | 2022-08-08 06:34 | 0.1 | O/C |  |  |  |  | -44781.2736 | -4478.1274 |  |  | No
11KV LAMIDO | TL |  |  | 2022-08-08 06:52 |  | O/C | ALH. SULE RELIEF 500KVA S/S ISOLATED ITSELF | NO | 2022-08-08 10:55 |  | 4:03 | 0 |  |  | Yes
11KV TOKARAWA | TL |  |  | 2022-08-08 06:56 |  | NO RI | CONDUCTED TREE TRIMMING ALONG THE LINE. | YES | 2022-08-08 13:20 |  | 6:24 | 0 |  |  | No
11KV TALAMIZ | TL |  |  | 2022-08-08 07:02 |  | O/C | OPENED JOGANA ISOLATOR | NO | 2022-08-08 10:13 |  | 3:11 | 0 |  |  | Yes
11KV SALLARI | TL |  |  | 2022-08-08 07:02 |  | E/F | REPOSITIONED B- PHASE CONDUCTOR AT SALLARI BABBA LAYI AND YAN ITACE 500KVA S/S WAS ISOLATED DUE TO 2NO. J&P DROPPED. | YES | 2022-08-08 09:22 |  | 2:20 | 0 |  |  | Yes
11KV YENLEMO | TL |  |  | 2022-08-08 07:16 |  | E/F | NOTHING FOUND | NO | 2022-08-08 11:21 |  | 4:05 | 0 |  |  | #N/A
11KV SANI ABACHA WAY | TL |  |  | 2022-08-08 02:31 | 0.8 | E/F | R AT DUTSE INJ. S/S | YES | 2022-08-08 09:30 |  | 6:59 | 0.23278 |  |  | No
11KV MUNDADU | TL |  |  | 2022-08-08 07:55 | 1 | E/F | AMENDED CUT B- PHASE JUMPER AT SHEKAR MAI DAKI | YES | 2022-08-08 15:19 |  | 7:24 | 0.30833 |  |  | No
11KV U/UKU | TL |  |  | 2022-08-08 07:55 | 3 | O/C | Removed a Bird that bridged the line @ Garu village, | YES | 2022-08-08 18:25 |  | 10:30 | 1.3125 |  |  | #N/A
33KV ZARIA ROAD | TL |  |  | 2022-08-08 07:49 | 19.3 | O/C | ISOLATED 33KV U/UKU | YES | 2022-08-08 07:55 |  | 0:06 | 0.080417 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-08 08:18 | 9 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 08:25 |  | 0:07 | 0.04375 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-08 08:30 | 9.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 08:30 |  | 0:00 | 0 |  |  | No
11KV PANSHEKARA | SE |  |  | 2022-08-08 08:53 |  |  | DUE TO DISCREPANCY OBSERVED R=B =2.7MW WHILE Y = 0MW. AMENDED CUT Y- PHASE JUMPER ON FIRST UPRISER. | YES | 2022-08-08 11:35 |  | 2:42 | 0 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-08 09:44 | 7 | O/C & E/F | ISOLATED BASCO 2.5MVA S/S DUE TO 2NO J&P DROPPED | NO | 2022-08-08 10:20 |  | 0:36 | 0.175 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-08 10:03 | 10.5 | O/C & E/F | OPENED GERAWA ISOLATOR | NO | 2022-08-08 11:54 |  | 1:51 | 0.80938 |  |  | Yes
33KV NNPC | TL |  | - | 2022-08-08 11:00 | 7.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 11:10 |  | 0:10 | 0.052083 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-08 11:13 | 0.8 | E/F | A BIRD TOUCH THE LINE AND FELL DOWN | YES | 2022-08-08 11:54 |  | 0:41 | 0.022778 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-08 11:35 | 7.5 | O/C & E/F | OPENED JOGANA ISOLATOR | NO | 2022-08-08 12:53 |  | 1:18 | 0.40625 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-08 11:46 | 18.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 11:55 |  | 0:09 | 0.11563 |  |  | Yes
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-08 11:41 | 1.4 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 11:51 |  | 0:10 | 0.0097222 |  |  | #N/A
33KV ZARIA ROAD | TL |  |  | 2022-08-08 12:12 | 24.8 | O/C & E/F | AMENDED CUT B- PHASE JUMPER AT KERD. | NO | 2022-08-08 14:41 |  | 2:29 | 2.5661 |  |  | Yes
33KV KOFAR GUGA | TL |  |  | 2022-08-08 12:30 | 4.1 | E/F | OPENED ALKAM ISOLATOR | NO | 2022-08-08 13:28 |  | 0:58 | 0.16514 |  |  | Yes
33KV BUK | TL |  |  | 2022-08-08 13:03 | 19 | O/C & E/F | NOTHING FOUND | NO | 2022-08-08 14:04 |  | 1:01 | 0.80486 |  |  | Yes
11KV HASSAN USMAN ROAD | TL |  |  | 2022-08-08 13:41 | 4.5 | E/F | REMOVED A BIRD THAT BRIDGED THE LINE AT GRA QTRS. | YES | 2022-08-08 15:20 |  | 1:39 | 0.30937 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-08 13:56 | 8.2 | E/F | AMENDED B- PHASE J&P AT TAJUDEEN 500KVA S/S | YES | 2022-08-08 14:30 |  | 0:34 | 0.19361 |  |  | Yes
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-08 14:07 | 3.9 | O/C & E/F | REPLACED SHATTERED Y- PHASE POT INSULATOR AT GARU MAKABARTA | YES | 2022-08-08 16:57 |  | 2:50 | 0.46042 |  |  | #N/A
11KV JAEN | TL |  |  | 2022-08-08 14:13 | 5.3 | O/C | KWANKWASIYYA 500KVA S/S ISOLATED ITSELF | NO | 2022-08-08 14:34 |  | 0:21 | 0.077292 |  |  | Yes
11KV AUDU BAKO | TL |  |  | 2022-08-08 14:20 | 2.2 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 14:30 |  | 0:10 | 0.015278 |  |  | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-08 14:43 | 7 | O/C | U/UKU 11KV FEEDER LEFT OUT FOR PATROL | NO | 2022-08-08 14:52 |  | 0:09 | 0.04375 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-08 14:46 | 3 | O/C & E/F | OPENED LAMBU ISOLATOR | NO | 2022-08-08 16:03 |  | 1:17 | 0.16042 |  |  | Yes
33KV KURNA | TL |  |  | 2022-08-08 15:06 | 1 | O/C & E/F | SHARUBUTU 500KVA S/S ISOLATED ITSELF | NO | 2022-08-08 15:49 |  | 0:43 | 0.029861 |  |  | Yes
11KV SABON GARI | TL |  |  | 2022-08-08 15:10 | 1.5 | O/C & E/F | Isolated Elison Hotel 500KVA S/S due to R-phase punctured XLPE cable | YES | 2022-08-08 22:02 |  | 6:52 | 0.42917 |  |  | No
33KV FLOUR MILLS | TL |  |  | 2022-08-08 15:25 | 20 | O/C | TRANSIENT | TRANSIENT | 2022-08-08 15:50 |  | 0:25 | 0.34722 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-08 15:29 | 2.8 | O/C & E/F | NOTHING FOUND | NO | 2022-08-08 16:07 |  | 0:38 | 0.073889 |  |  | #N/A
11KV NOMANS LAND | SE |  |  | 2022-08-08 16:27 | 2 |  | DUE TO S/S ON FIRE AT NOMANS LAND, ISOLATED MTN 50KVA BOOSTER S/S DUE TO 2NO. J&P DROPPED. | NO | 2022-08-08 17:21 |  | 0:54 | 0.075 |  |  | #N/A
33KV FLOUR MILLS | TL |  |  | 2022-08-08 17:10 | 14.5 | O/C | HEAVY EXPLOSION ALONG 15MVA TR3 AFFECTING LAMIDO 11KV FEEDER | NO | 2022-08-08 17:23 |  | 0:13 | 0.1309 |  |  | Yes
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-08 17:16 | 16.2 | O/C & E/F | Apened A11 Isolator, | NO | 2022-08-08 18:13 |  | 0:57 | 0.64125 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-08 17:30 | 2.6 | O/C & E/F | Removed a Bird that bridged the line @ Bakin Kogi, | YES | 2022-08-12 21:50 |  | 100:20 | 10.8694 |  |  | #N/A
33KV DANGOTE | TL |  |  | 2022-08-08 17:31 | 16 | O/C & E/F | The tripping was due to closing Bagco I 2.5MVA S/S earlier dropped 2no J&P after tested OK, it was opened back | YES | 2022-08-08 18:13 |  | 0:42 | 0.46667 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-08 18:53 | 10.5 | O/C & E/F | FLOUR MILLS 1MVA S/S ISOLATED ITSELF | YES | 2022-08-08 08:24 |  | -0.43681 | -4.5865 |  |  | No
33KV GANO | SE |  |  | 2022-08-08 19:11 | 1.8 |  | Discrepancy observed R= 1.8MW while Y=B=9.6MW, Amended R-phase cut jumper on Polac isolator, |  | 2022-08-08 21:40 |  | 2:29 | 0.18625 |  |  | Yes
33KV MAMMAN NASIR | TL |  |  | 2022-08-08 19:19 |  | E/F | NOTHING FOUND | NO | 2022-08-09 09:20 |  | 14:01 | 0 |  |  | No
33KV GANO | SE |  |  | 2022-08-08 21:41 | 1.8 |  | Discrepancy observed R= 1.8MW while Y=B=9.6MW, Amended R-phase cut jumper on Polac isolator,AMENDED CUT B PHASE JUMPER AT MAKOLE | YES | 2022-08-09 09:18 |  | 11:37 | 0.87125 |  |  | No
33KV GASKIYA | TL |  |  | 2022-08-08 20:12 | 12 | O/C & E/F | OPENED GERAWA LEG | NO | 2022-08-08 20:33 |  | 0:21 | 0.175 |  |  | Yes
11KV MAJE | TL |  |  | 2022-08-08 20:51 | 3.1 | O/C | REMOVED A BRANCH OF TREE AT HAMZA ABDULLAHI MOSQUE ALONG NGURU ROAD | YES | 2022-08-09 12:55 |  | 16:04 | 2.0753 |  |  | No
33KV GAYA | TL |  |  | 2022-08-08 21:20 | 1.4 | E/F | tree trimming condcuted on the line | YES | 2022-08-09 09:52 |  | 12:32 | 0.73111 |  |  | No
33KV WUDIL | TL |  |  | 2022-08-08 21:20 | 2.5 | O/C | GAYA LEFT OUT FOR PATROL | YES |  |  | -44781.8889 | -111954.7222 |  |  | No
11KV NAKOWA | TL |  |  | 2022-08-08 21:25 | 2.9 | O/C & E/F |  |  |  |  | -44781.8924 | -129867.4878 |  |  | No
11KV JAMARE | TL |  |  | 2022-08-08 21:30 |  | O/C & E/F |  |  |  |  | -44781.8958 | 0 |  |  | #N/A
33KV GARKO | TL |  |  | 2022-08-08 22:35 | 2.4 | E/F | TREE TRIMMING CONDUCTED AT TUDUN GUSAU AND A BIRD REMOVED FROM THE LINE AT YAN LAHADI | YES | 2022-08-09 12:30 |  | 13:55 | 1.3917 |  |  | No
33KV MUSAWA | TL |  |  | 2022-08-08 22:38 |  | E/F | OPENED MUSAAWA BICHI AND KUSADA LEGS | NO | 2022-08-09 09:25 |  | 10:47 | 0 |  |  | No
33KV TAMBURAWA W/WORKS | SE |  |  | 2022-08-08 23:02 |  |  | Tamburawa W/Plant requested to opened Tamburawa W/Plant 11kV fdr due to tripping on their breaker, | YES | 2022-08-08 21:50 |  | -0.05 | 0 |  |  | #N/A
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-08 23:03 | 3.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-12 23:13 |  | 96:10 | 14.425 |  |  | #N/A

## 9
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
11KV SAGAGI | TL |  |  | 2022-08-09 00:25 | 0.4 | E/F | AMENDED R PHASE JUMPER AT SCHOOL OF NURSING T OFF | YES | 2022-08-09 11:38 |  | 11:13 | 0.18694 |  |  | No
33KV BIRNIWA | TL |  |  | 2022-08-09 00:33 | 0.4 | E/F | Opened Rungumau isolato | NO | 2022-08-09 08:32 |  | 7:59 | 0.13306 |  |  | No
33KV KWANKWASO | TL |  |  | 2022-08-09 00:50 | 3.4 | O/C & E/F | Opened Rungumau isolato | NO | 2022-08-09 08:38 |  | 7:48 | 1.105 |  |  | Yes
33KV MAI ADUA | TL |  |  | 2022-08-09 00:50 | 1.5 | E/F | ISOLATED MAI ADUA, ZANGO, FAGO AND SANDAMU LEGS | NO | 2022-08-09 09:38 |  | 8:48 | 0.55 |  |  | No
11KV FANISAU | TL |  |  | 2022-08-09 01:00 | 1.7 | E/F | ISOLATED WALAWA AND RIMAYE T- OFF'S. | NO | 2022-08-09 18:09 |  | 17:09 | 1.2148 |  |  | No
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-09 01:34 | 9.4 | O/C & E/F | Opened Hawan Dawaki Isolator, | NO | 2022-08-09 05:10 |  | 3:36 | 1.41 |  |  | Yes
33KV MASHI | TL |  |  | 2022-08-09 01:37 | 1.8 | E/F | OPENED GODAI LEG | NO | 2022-08-09 09:39 |  | 8:02 | 0.6025 |  |  | No
33KV SUMAILA | TL |  |  | 2022-08-09 02:30 | 2.1 | E/F |  |  |  |  | -44782.1042 | -94042.4187 |  |  | No
33KV AJIWA WATER WORKS | TL |  |  | 2022-08-09 07:07 | 1 | O/C & E/F | AHUTA HOTEL 500KVA S/S dropped 2no, third one isolated | YES | 2022-08-09 09:28 |  | 2:21 | 0.097917 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-09 07:10 | 5.7 | E/F | OPENED HALIRU HAKILU ISOLATOR | NO | 2022-08-09 07:53 |  | 0:43 | 0.17021 |  |  | Yes
11KV SHARADA INDUSTRIAL | TL |  |  | 2022-08-09 08:30 | 3 | E/F | BYPASSED Y PHASE CUT UMPER AT GIDAN MAZA ISOLATOR, APPROVAL GIVEN AT 11:12 | YES | 2022-08-09 16:53 |  | 8:23 | 1.0479 |  |  | No
11KV SANI MAINAGGE | TL |  |  | 2022-08-09 08:38 | 2.5 | O/C & E/F | NOTHING FOUND | NO | 2022-08-09 19:43 |  | 11:05 | 1.1545 |  |  | No
33KV FLOUR MILLS | TL |  |  | 2022-08-09 08:44 | 12 | O/C | TRANSIENT | TRANSIENT | 2022-08-09 08:55 |  | 0:11 | 0.091667 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-09 08:55 | 2 | O/C & E/F | OPENED TARAU ISOLATOR | NO | 2022-08-09 13:35 |  | 4:40 | 0.38889 |  |  | Yes
11KV CHIRANCI | TL |  |  | 2022-08-09 09:00 | 6.7 | O/C & E/F | CHIRANCHI GABAS 500KVA S/S DROPPED 1NO, AMENDED | YES | 2022-08-09 09:10 |  | 0:10 | 0.046528 |  |  | Yes
33KV SPANISH 2 | TL |  |  | 2022-08-09 09:21 | 19.5 | O/C | CUT Y PHASE UPRISER OBSERVED AFTER INSPECTION, AMENDED | YES | 2022-08-09 12:56 |  | 3:35 | 2.9115 |  |  | Yes
33KV CLUB | SE |  |  | 2022-08-09 09:47 |  |  | DUE TO DISCREPANCY OBSERVED, CUT Y- PHASE JUMPER WAS AMENDED AT K/NASSARAWA FLYOVER | YES | 2022-08-09 21:08 |  | 11:21 | 0 |  |  | No
33KV NNPC | SE |  |  | 2022-08-09 10:05 | 7.5 |  | TISHAMA OLD 500KVA S/S ON FIRE, OPENED JOGANA ISOLATOR | NO | 2022-08-09 11:50 |  | 1:45 | 0.54687 |  |  | Yes
11KV MAIDUGURI ROAD | SE |  |  | 2022-08-09 10:10 | 0.1 |  | CUT CONDUCTOR ON THE GROUND, AMENDED | YES | 2022-08-09 11:50 |  | 1:40 | 0.0069444 |  |  | Yes
11KV FARAWA | SE |  |  | 2022-08-09 11:15 | 4 |  | CUT CONDUCTOR ON THE GROUND, AMENDED | YES | 2022-08-09 11:50 |  | 0:35 | 0.097222 |  |  | Yes
11KV ORTHOPAEDIC | TL |  |  | 2022-08-09 10:25 | 2.6 | E/F | AMENDED R PHASE J&P AT 500KVA S/S MALAMAI | YES | 2022-08-09 16:48 |  | 6:23 | 0.69153 |  |  | No
33KV DANGOTE | TL |  |  | 2022-08-09 10:53 | 15 | O/C | TRANSIENT | TRANSIENT | 2022-08-09 10:56 |  | 0:03 | 0.03125 |  |  | Yes
33KV BIRNIWA | TL |  |  | 2022-08-09 12:30 | 0.7 | E/F | OPENED GAYIN LEG | NO | 2022-08-09 21:01 |  | 8:31 | 0.2484 |  |  | No
33KV GARKO | TL |  |  | 2022-08-09 12:37 | 0.5 | O/C & E/F | REMOVED A LIZARD THAT BRIDGED THE LINE AT LAMIRE VILLAGE. | YES | 2022-08-09 18:25 |  | 5:48 | 0.12083 |  |  | Yes
11KV DANLADI NASIDI | SE |  |  | 2022-08-09 13:17 |  |  | DISCREPANCY OBSERVED B = 1.0MW, R=Y=2.3MW. PATROLLED NOTHING AND ALL PHASES OK. | NO | 2022-08-09 18:47 |  | 5:30 | 0 |  |  | No
33KV JAHUN | TL |  |  | 2022-08-09 14:02 | 3.2 | E/F | OPENED SHUWARIN AND DANTATA ISOLATORS | NO | 2022-08-09 18:20 |  | 4:18 | 0.57333 |  |  | Yes
33KV KARAYE | TL |  |  | 2022-08-09 14:30 | 4.1 | O/C & E/F | OPENED DANGORA ISOLATOR | NO | 2022-08-09 17:58 |  | 3:28 | 0.59222 |  |  | Yes
33KV IDH | TL |  |  | 2022-08-09 15:30 | 11.6 | E/F | BIRDS BRIDGED THE LINE AND FELL DOWN AT PRP INJ S/S SWITCH YARD | NO | 2022-08-09 15:38 |  | 0:08 | 0.064444 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-09 15:28 | 2 | E/F | BUK Isolator was opened | NO | 2022-08-10 14:18 |  | 22:50 | 1.9028 |  |  | No
33KV CBN | TL |  |  | 2022-08-09 17:00 | 9.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-09 17:12 |  | 0:12 | 0.079167 |  |  | Yes
11KV MAIDUGURI ROAD | TL |  |  | 2022-08-09 17:17 |  | O/C & E/F | RETERMINATED PUNCTURED UNDER GROUND CABLE | NO | 2022-08-10 18:45 |  | 25:28 | 0 |  |  | No
33KV AJIWA WATER WORKS | SE |  |  | 2022-08-09 19:37 | 5.5 |  | DUE TO ARCING ON AHUTA HOTEL ISOLATOR, THE ISOLATOR WAS OPENED. | NO | 2022-08-09 20:03 |  | 0:26 | 0.099306 |  |  | Yes
11KV INDEPENDENCE | TL |  |  | 2022-08-09 20:20 | 1.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-09 20:48 |  | 0:28 | 0.031111 |  |  | Yes
33KV GARKO | TL |  |  | 2022-08-09 20:30 | 3 | E/F | DARKI, JIGAWARE, GARKO LEGS WERE ISOLATED. | NO | 2022-08-10 09:45 |  | 13:15 | 1.6563 |  |  | No
33KV GEZAWA | TL |  |  | 2022-08-09 21:09 | 3.2 | O/C & E/F | OPENED ZAURAN DANBABA ISOLATOR | NO | 2022-08-09 22:57 |  | 1:48 | 0.24 |  |  | Yes
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 10
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV BAGAUDA | TL |  |  | 2022-08-10 02:28 | 3 | E/F | OPENED TAMBURAWA ISOLATOR | NO | 2022-08-10 07:38 |  | 5:10 | 0.64583 |  |  | Yes
33KV MAMMAN NASIR | TL |  |  | 2022-08-10 02:58 | 1.5 | E/F |  |  |  |  | -44783.1236 | -67174.6854 |  |  | No
33KV DUTSE | TL |  |  | 2022-08-10 03:56 | 4.4 | E/F | CGC TILES COMPANY ISOLATOR OPENED. | NO | 2022-08-10 08:52 |  | 4:56 | 0.90444 |  |  | Yes
33KV SUMAILA | TL |  |  | 2022-08-10 04:03 | 1.5 | E/F | OPENED RUNGUMAU ISOLATOR | NO | 2022-08-10 08:10 |  | 4:07 | 0.25729 |  |  | Yes
33KV GANO | TL |  |  | 2022-08-10 04:04 | 6.6 | E/F | ISOLATED DORAWA NA'ABBA T-OFF DUE TO R- PHASE CUT LINE FUSE ELEMENT. | NO | 2022-08-10 06:34 |  | 2:30 | 0.6875 |  |  | Yes
33KV BIRNIN KUDU | TL |  |  | 2022-08-10 04:31 | 3.2 | E/F | OPENED DANMASARA ISOLATOR | NO | 2022-08-10 08:29 |  | 3:58 | 0.52889 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-10 04:34 | 2.4 | E/F | Shuwarin and Dantata legs,were isolated | NO | 2022-08-10 09:42 |  | 5:08 | 0.51333 |  |  | Yes
33KV AJIWA WATER WORKS | TL |  |  | 2022-08-10 05:05 | 3.1 | E/F | Branch of tree bridge the line removedat Shagumba village | YES | 2022-08-10 10:35 |  | 5:30 | 0.71042 |  |  | Yes
33KV BUK | TL |  |  | 2022-08-10 05:33 | 12 | O/C & E/F | NOTHING FOUND | NO | 2022-08-10 07:33 |  | 2:00 | 1 |  |  | Yes
33KV CLUB | SE |  |  | 2022-08-10 06:07 |  |  | DUE TO DISCREPANCY OBSERVED R = 0MW WHILE Y=B = 4.0MW. |  | 2022-08-10 11:11 |  | 5:04 | 0 |  |  | Yes
33KV FALGORE | TL |  |  | 2022-08-10 07:12 | 2.6 | O/C & E/F | OPENED KWANAR T/WADA ISOLATOR | NO | 2022-08-10 08:46 |  | 1:34 | 0.16972 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-10 07:14 | 3.2 | O/C & E/F | OPENED TARAU ISOLATOR | NO | 2022-08-10 08:47 |  | 1:33 | 0.20667 |  |  | Yes
33KV NNPC | TL |  |  | 2022-08-10 09:12 |  | O/C & E/F | Tunshama leg was isolated | NO | 2022-08-10 11:04 |  | 1:52 | 0 |  |  | Yes
33KV GAYA | TL |  |  | 2022-08-10 10:10 | 1.2 | E/F | KUT ISOLATOR WAS OPENED | NO | 2022-08-10 17:22 |  | 7:12 | 0.36 |  |  | Yes
33KV WUDIL | TL |  |  | 2022-08-10 10:10 | 2.6 | E/F | TRANSIENT | TRANSIENT | 2022-08-10 10:40 |  | 0:30 | 0.054167 |  |  | Yes
33KV IDH | PM | 2022-08-10 10:30 | 2022-08-10 13:30 | 2022-08-10 10:50 | 12 |  | For safe working space to carry out substation weeding at 33/11KV IDH & PRP Substation |  | 2022-08-10 12:27 |  | 1:37 | 0.80833 | Yes
33KV DAWAKI | PM | 2022-08-10 10:00 | 2022-08-10 16:00 | 2022-08-10 10:57 | 3.2 |  | S.G no 28815 was issued on 33KV Dawaki leg to carry out tree trimming on 33KV Dawaki leg, L/L=3.2MW.. |  | 2022-08-10 19:08 |  | 8:11 | 1.0911 | No | 2:11
33KV NNPC | PM | 2022-08-10 10:00 | 2022-08-10 10:30 | 2022-08-10 11:05 | 3.3 |  | For safe working space to open jumper at yan itace T-off to replaced cut conductor |  |  |  | -44783.4618 | -147785.424 | Yes
11KV BADAWA | TL |  |  | 2022-08-10 12:19 | 3 | O/C | TRANSIENT | TRANSIENT | 2022-08-10 12:30 |  | 0:11 | 0.022917 |  |  | Yes
33KV CBN | PM |  |  | 2022-08-10 12:33 | 8.4 | O/C | TRANSIENT | TRANSIENT | 2022-08-10 12:45 |  | 0:12 | 0.07 | No | 0:12
33KV KAITA | TL |  |  | 2022-08-10 12:35 | 4.7 | E/F | Bird bridge the line and removed at Afdin company | YES | 2022-08-10 13:38 |  | 1:03 | 0.20563 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-10 12:43 | 15.6 | E/F | NOTHING FOUND | TRANSIENT | 2022-08-10 14:49 |  | 2:06 | 1.365 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-10 12:17 | 17 | O/C |  |  |  |  | -44783.5118 | -761319.7007 |  |  | No
33KV MTN | PM | 2022-08-10 13:00 | 2022-08-10 13:30 | 2022-08-10 13:20 | 12.5 |  | For safe working space to carry out weed control at Brisco |  | 2022-08-10 14:16 |  | 0:56 | 0.48611 | No | 0:26
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-10 13:37 | 4.1 | O/C & E/F | Dr. Jamil feeder was isolated | NO | 2022-08-10 15:13 |  | 1:36 | 0.27333 |  |  | #N/A
33KV GEZAWA | TL |  |  | 2022-08-10 13:40 | 3.8 | O/C & E/F | Zaura isolator was opened | NO | 2022-08-10 16:35 |  | 2:55 | 0.46181 |  |  | Yes
33KV KURNA | TL |  |  | 2022-08-10 13:50 | 2.5 | O/C & E/F | 33Kv Dawanau feeder was isolator | NO | 2022-08-10 14:10 |  | 0:20 | 0.034722 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-10 13:52 | 3 | E/F | Tree trimming at Airport and Branch of tree was removed |  | 2022-08-10 14:58 |  | 1:06 | 0.1375 |  |  | Yes
33KV BAGAUDA | TL |  |  | 2022-08-10 13:52 | 6 | E/F | Tamburawa isolator was opened | NO | 2022-08-10 17:01 |  | 3:09 | 0.7875 |  |  | Yes
33KV GARKO | TL |  |  | 2022-08-10 14:17 | 2.9 | E/F | Garko & Rimi legs isolated | NO | 2022-08-10 17:19 |  | 3:02 | 0.36653 |  |  | Yes
33KV KWANKWASO | TL |  |  | 2022-08-10 14:44 | 1.8 | E/F | Kafin Agur isolator was isolated | NO | 2022-08-10 16:36 |  | 1:52 | 0.14 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-10 14:45 | 16 | O/C | TRANSIENT | TRANSIENT | 2022-08-10 14:55 |  | 0:10 | 0.11111 |  |  | Yes
33KV KURNA | TL |  |  | 2022-08-10 15:00 | 10.3 | E/F |  |  |  |  | -44783.625 | -461271.3375 |  |  | No
33KV NNPC | TL |  |  | 2022-08-10 15:29 | 5.5 | E/F | Jogana isolator was opened | NO | 2022-08-10 16:10 |  | 0:41 | 0.1566 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-10 15:31 | 11 | O/C & E/F | Nothing found | NO | 2022-08-10 17:18 |  | 1:47 | 0.81736 |  |  | Yes
33KV GASKIYA | TL |  |  | 2022-08-10 15:56 | 14.4 | E/F |  |  |  |  | -44783.6639 | -644884.76 |  |  | No
33KV KAITA | TL |  |  | 2022-08-10 16:18 | 5.8 | E/F | Kaita and High Court Isolator was opened | NO | 2022-08-10 17:07 |  | 0:49 | 0.19736 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-10 16:36 | 14.4 | E/F | NOTHING FOUND | NO | 2022-08-10 19:01 |  | 2:25 | 1.45 |  |  | Yes
11KV INDEPENDENCE | TL |  |  | 2022-08-10 17:19 |  | E/F | RETERMINATED PUNCTURED UPRISER CABLE | YES | 2022-08-10 20:52 |  | 3:33 | 0 |  |  | Yes
33KV LAW SCHOOL | TL |  |  | 2022-08-10 17:34 | 2.9 | E/F | OPENED TARAU ISOLATOR | NO | 2022-08-10 19:46 |  | 2:12 | 0.26583 |  |  | Yes
11KV SABON GARI | SE |  |  | 2022-08-10 17:47 | 2.5 |  | Old Kowa 500Kva s/s on fire, ISOLATED | YES | 2022-08-10 18:05 |  | 0:18 | 0.03125 |  |  | Yes
33KV GEZAWA | TL |  |  | 2022-08-10 18:13 | 2.7 | O/C & E/F | OPENED ZAUREN DANBABA ISOLATOR | NO | 2022-08-11 03:04 |  | 8:51 | 0.99563 |  |  | No
33KV SMALL SCALE | TL |  |  | 2022-08-10 18:03 | 3.6 | O/C | GEZAWA LEFT OUT FOR PATROL | YES | 2022-08-10 18:13 |  | 0:10 | 0.025 |  |  | Yes
33KV BUK | TL |  |  | 2022-08-10 18:14 |  | O/C & E/F | NOTHING FOUND | NO | 2022-08-10 22:05 |  | 3:51 | 0 |  |  | Yes
33KV CBN | TL |  |  | 2022-08-10 18:00 | 6.2 | E/F | OPENED HALLIRU AKILU ISOLATOR | NO | 2022-08-10 18:40 |  | 0:40 | 0.17222 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-10 19:57 | 12 | O/C | TRANSIENT | TRANSIENT | 2022-08-10 20:12 |  | 0:15 | 0.125 |  |  | Yes
33KV MUSAWA | TL |  |  | 2022-08-10 20:20 | 5.2 | E/F | OPENED BICHI AND KUSADA LEGS | NO | 2022-08-10 21:45 |  | 1:25 | 0.30694 |  |  | Yes
11KV KOKI | TL |  |  | 2022-08-10 21:50 |  | O/C & E/F | AMENDED R PHASE J&P AT K/MAZUGAL 500KVA S/S | YES | 2022-08-10 01:05 |  | -0.86458 | 0 |  |  | No
11KV HASSAN USMAN ROAD | TL |  |  | 2022-08-10 23:40 | 6.4 | E/F | 11kV H/Usman feeder was tried and stayed after separated Twisted conductor at CBN Junction. TE Urban approved. | YES | 2022-08-11 12:31 |  | 12:51 | 3.4267 |  |  | No
33KV SUMAILA | TL |  |  | 2022-08-10 23:46 | 2.1 | E/F | 33kV Sumaila feeder was tried & stayed okay, Rungumau isolator was opened. RE JGS approved. | NO | 2022-08-11 11:50 |  | 12:04 | 1.0558 |  |  | No
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 11
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
33KV BIRNIWA | TL |  |  | 2022-08-11 00:50 | 1 | E/F | 33kV Birniwa feeder was tried and stayed after opened Gari Magaji and Tasheguwa legs. RE JGN approved. | YES | 2022-08-11 10:40 |  | 9:50 | 0.40972 |  |  | No
33KV KARAYE | TL |  |  | 2022-08-11 00:46 | 3.3 | O/C & E/F | 33kV Karaye feeder was tried and stayed after opened Dangora isolator. RE Dangora approved. | NO | 2022-08-11 09:41 |  | 8:55 | 1.226 |  |  | No
33KV GUMEL | TL |  |  | 2022-08-11 01:10 | 1 | E/F | NOTHING FOUND | NO | 2022-08-11 12:08 |  | 10:58 | 0.45694 |  |  | No
33KV KAFIN HAUSA | TL |  |  | 2022-08-11 01:13 | 3 | E/F | 33kV K/Hausa feeder tried and stayed after opened Ganuwar Kuka and Yanleman legs. It earlier tripped on E/F with 2.3MW. RE JGN approved. | NO | 2022-08-11 09:57 |  | 8:44 | 1.0917 |  |  | No
33KV HADEJIA | TL |  |  | 2022-08-11 01:27 | 3.4 | E/F | 33kV Hadejia feeder was tried & stayed okay, G/Leda isolator was opened. RE JGN approved. | YES | 2022-08-11 09:25 |  | 7:58 | 1.1286 |  |  | No
11KV BACHIRAWA | TL |  |  | 2022-08-11 01:45 |  | O/C & E/F |  |  |  |  | -44784.0729 | 0 |  |  | No
33KV KWANKWASO | TL |  |  | 2022-08-11 02:55 | 5 | O/C & E/F | 33kV Kwankwaso feeder was tried & stayed okay, Garu isolator was opened. RE Panshekara approved. | NO | 2022-08-11 09:10 |  | 6:15 | 1.3021 |  |  | Yes
33KV JAHUN | TL |  |  | 2022-08-11 02:50 | 2.4 | E/F | 33kV Jahun feeder was tried & stayed okay, Dantata & Shuwarin isolators were opened. RE JGS approved. | NO | 2022-08-11 11:50 |  | 9:00 | 0.9 |  |  | No
33KV GAGARAWA | TL |  |  | 2022-08-11 02:10 | 1.8 | O/C & E/F | OPENED MAIGATARI GARKI AND BOSUWA LEGS | NO | 2022-08-11 08:42 |  | 6:32 | 0.49 |  |  | No
33KV GASKIYA | TL |  |  | 2022-08-11 04:14 | 10.8 | O/C & E/F | 33kV Gaskiya feeder was tried and stayed after opened Nassarawa and Gerawa isolators. RE Kawaji approved. | NO | 2022-08-11 09:32 |  | 5:18 | 2.385 |  |  | Yes
33KV FLOUR MILLS | TL |  |  | 2022-08-11 04:16 | 12 | O/C & E/F | 33kV F/Mills feeder was tried and stayed after opened jumper at kwanar Yantifa due to 5no Broken HT Poles, faulty portion isolated. RE S/Gari approved. | YES | 2022-08-11 11:57 |  | 7:41 | 3.8417 |  |  | No
33KV NNPC | TL |  |  | 2022-08-11 04:19 | 3.5 | O/C & E/F | JOGANA ISOLATOR WAS OPENED | NO | 2022-08-11 11:06 |  | 6:47 | 0.98924 |  |  | No
33KV IDH | TL |  |  | 2022-08-11 04:18 | 8.4 | O/C & E/F | 33kV IDH feeder was tried and stayed after opened Hajj Camp and Flying Training School isolator. RE S/Gari approved | NO | 2022-08-11 10:19 |  | 6:01 | 2.1058 |  |  | No
33KV SMALL SCALE | TL |  |  | 2022-08-11 04:20 | 5.9 | O/C & E/F | TRANSIENT | TRANSIENT | 2022-08-11 05:08 |  | 0:48 | 0.19667 |  |  | Yes
33KV MTN | TL |  |  | 2022-08-11 04:27 | 13.5 | O/C & E/F | 33kV MTN feeder was tried and stayed after isolated MTN 1MVA S/S due to 2no J&P dropped. RE S/Gari approved. | YES | 2022-08-11 10:51 |  | 6:24 | 3.6 |  |  | No
33KV GAYA | TL |  |  | 2022-08-11 04:05 |  | O/C | 33kV Gaya feeder was tried and stayed after replaced 2no Pot insulators at Wudil Inj S/S also KUT isolator in opened position. RE Hotoro approved. | YES | 2022-08-11 16:11 |  | 12:06 | 0 | No | 12:06 | No
33KV WUDIL | TL |  |  | 2022-08-11 04:05 | 1 | E/F | GAYA LEFT OUT FOR PATROL | NO | 2022-08-11 05:55 |  | 1:50 | 0.076389 | No | 1:50 | Yes
11KV ARMY BARRACKS | TL |  |  | 2022-08-11 04:24 | 3 | E/F | NOTHING FOUND | NO | 2022-08-11 12:36 |  | 8:12 | 1.025 | No | 8:12 | No
33KV GANO | TL |  |  | 2022-08-11 04:05 | 8 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 05:55 |  | 1:50 | 0.61111 |  |  | Yes
11KV AHMADU BELLO | TL |  |  | 2022-08-11 04:17 | 3.3 | E/F | AMENDED B PHASE J&P AT ALU AVENUE 500KVA | YES | 2022-08-11 14:48 |  | 10:31 | 1.446 | No | 10:31 | No
11KV RACE COURSE | TL |  |  | 2022-08-11 04:18 | 1.4 | O/C |  |  |  |  | -44784.1792 | -62697.8508 |  |  | No
11KV AUDU BAKO | TL |  |  | 2022-08-11 04:22 | 1.6 | E/F | 11kV A/Bako feeder was tried and stayed after nothing found. TE HQ approved. | NO | 2022-08-11 10:08 |  | 5:46 | 0.38444 |  |  | No
11KV BADAWA | TL |  |  | 2022-08-11 04:25 | 3.3 | O/C | NOTHING | NO | 2022-08-11 11:38 |  | 7:13 | 0.99229 |  |  | No
11KV MURTALA MOHD | TL |  |  | 2022-08-11 04:27 | 0.8 | O/C | 33kV CBN feeder was tried and stayed after opened Aliyu Bin Abi Talib Isolator. RE KNC approved. | NO | 2022-08-11 09:27 |  | 5:00 | 0.16667 | No | 5:00 | #N/A
11KV BANK ROAD | TL |  |  | 2022-08-11 04:22 | 2 | O/C | 11kV A/Bako feeder was tried and stayed after nothing found. TE HQ approved. | NO | 2022-08-11 10:08 |  | 5:46 | 0.48056 |  |  | No
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-11 03:14 | 4 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 03:26 |  | 0:12 | 0.033333 |  |  | #N/A
33KV BIRNIN KUDU | TL |  |  | 2022-08-11 03:22 | 3.1 | E/F | DAN MASARA OPENED | NO | 2022-08-11 11:50 |  | 8:28 | 1.0936 |  |  | No
11KV KOFAR NA'ISA | TL |  |  | 2022-08-11 04:14 | 2.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 07:48 |  | 3:34 | 0.38639 |  |  | #N/A
11KV KOFAR NASSARAWA | TL |  |  | 2022-08-11 04:15 | 1.6 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 07:51 |  | 3:36 | 0.24 |  |  | Yes
11KV AJASA | TL |  |  | 2022-08-11 04:16 | 1.4 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 07:52 |  | 3:36 | 0.21 |  |  | Yes
11KV IBRAHIM TAIWO | TL |  |  | 2022-08-11 04:16 | 1.8 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 07:50 |  | 3:34 | 0.2675 |  |  | Yes
11KV CITY | TL |  |  | 2022-08-11 04:18 | 1.4 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 07:49 |  | 3:31 | 0.20514 |  |  | Yes
11KV U/UKU | TL |  |  | 2022-08-11 04:26 | 3 | O/C & E/F | 11kV U/Uku feeder was tried and stayed after removed a bat Garu Village also B Phase Jumper reposition at Baba Mohd T-off. TE Hotoro approved. | YES | 2022-08-11 13:16 |  | 8:50 | 1.1042 |  |  | #N/A
33KV ZARIA ROAD | TL |  |  | 2022-08-11 04:26 | 16 | O/C & E/F | NOTHING FOUND | NO | 2022-08-11 09:27 |  | 5:01 | 3.3444 |  |  | Yes
11KV NOMANS LAND | TL |  |  | 2022-08-11 04:28 | 1.6 | O/C | 11kV Nomansland feeder after isolated Zungeru/Court Road 500kVA S/S due to R Phase burnt XLPE Cable. | YES | 2022-08-11 16:51 |  | 12:23 | 0.82556 |  |  | #N/A
11KV FANISAU | TL |  |  | 2022-08-11 04:30 | 1.6 | E/F | Ungogo isolator was opened | NO | 2022-08-11 19:06 |  | 14:36 | 0.97333 |  |  | No
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-11 04:32 | 10.1 | O/C & E/F | 33kV R/Zaki feeder was tried and stayed after opened A11 isolator. RE Kabuga approved. | NO | 2022-08-11 09:46 |  | 5:14 | 2.2024 |  |  | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-11 04:36 | 1.7 | O/C & E/F | NOTHING FOUND | NO | 2022-08-11 11:08 |  | 6:32 | 0.46278 |  |  | #N/A
33KV CBN | TL |  |  | 2022-08-11 04:27 | 5.8 | E/F |  |  |  |  | -44784.1854 | -259748.2754 |  |  | No
33KV KURNA | TL |  |  | 2022-08-11 04:32 | 10.2 | O/C & E/F | 33kV Kurna feeder was tried and stayed after opened Sharubutu Isolator. RE Dala approved. | NO | 2022-08-11 09:41 |  | 5:09 | 2.1888 |  |  | Yes
33KV BUK | TL |  |  | 2022-08-11 04:34 | 1.7 | O/C & E/F |  |  |  |  | -44784.1903 | -76133.1235 |  |  | No
33KV BAGAUDA | TL |  |  | 2022-08-11 04:27 | 2.8 | E/F | 33kV BUK feeder was tried and stayed after opened K/Famfo isolator. RE Kabuga approved. | NO | 2022-08-11 09:27 |  | 5:00 | 0.58333 |  |  | Yes
33KV ATM | TL |  |  | 2022-08-11 04:32 | 5.1 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 09:15 |  | 4:43 | 1.0023 |  |  | Yes
33KV SPANISH 2 | TL |  |  | 2022-08-11 04:40 | 17.5 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 10:13 |  | 5:33 | 4.0469 |  |  | Yes
33KV DANGOTE | TL |  |  | 2022-08-11 04:42 | 4.8 | O/C & E/F | R PHASE JUMPER TOUCHING CONCREATE POLE ALONG BUK ROAD. | YES | 2022-08-11 17:13 |  | 12:31 | 2.5033 |  |  | No
33KV ANGELS | TL |  |  | 2022-08-11 04:50 | 13.2 | E/F | NOTHING | NO | 2022-08-11 09:15 |  | 4:25 | 2.4292 |  |  | Yes
11KV SANI MAINAGGE | TL |  |  | 2022-08-11 04:32 | 1.3 | O/C | Tree trimming was conducted on the line | YES | 2022-08-11 19:35 |  | 15:03 | 0.81521 |  |  | No
11KV DANDAGORO | TL |  |  | 2022-08-11 04:30 | 2.4 | E/F | 11kV Dandagoro feeder was tried and stayed after opened Car Wash isolator. TE Urban approved. | NO | 2022-08-11 10:50 |  | 6:20 | 0.63333 |  |  | No
33KV GARKO | TL |  |  | 2022-08-11 04:30 |  | E/F | 33kV Garko feeder was tried and stayed after opened suspected Garko, Darki and Jigaware legs. RE KNE Hotoro approved. | NO | 2022-08-11 13:20 |  | 8:50 | 0 |  |  | No
11KV G.R.A. | TL |  |  | 2022-08-11 04:35 | 3 | O/C |  |  |  |  | -44784.191 | -134352.5729 |  |  | #N/A
33KV WATARI | TL |  |  | 2022-08-11 05:17 | 0.4 | E/F | 33kV Watari feeder was tried and stayed after amended 1no B Phase J&P at Saraka 200kVA S/S. RE KTC approved. | YES | 2022-08-11 13:29 |  | 8:12 | 0.13667 |  |  | No
11KV TUDUN MURTALA | TL |  |  | 2022-08-11 05:48 | 1.2 | O/C & E/F |  |  |  |  | -44784.2417 | -53741.09 |  |  | No
11KV YANLEMO | TL |  |  | 2022-08-11 04:20 | 1.9 | E/F | Titin College 500KVA S/S was isolated due to burnt Yellow and Blue phases J&P Carriers | YES | 2022-08-11 20:27 |  | 16:07 | 1.2759 |  |  | No
11KV LOW COST | TL |  |  | 2022-08-11 07:58 | 1.4 | E/F | 11kV L/Cost feeder was tried and stayed after replaced Y Phase Pin Insulator at rahusa Relief 300kVA S/S. TE KT City approved. | NO | 2022-08-11 10:25 |  | 2:27 | 0.14292 |  |  | Yes
11KV INDEPENDENCE | TL |  |  | 2022-08-11 04:21 | 0.6 | O/C | Miller rd twisted conductor separated removed branch of tree removed near kwankwaso resident | YES | 2022-08-11 06:05 |  | 1:44 | 0.043333 |  |  | Yes
11KV MAIMALARI | TL |  |  | 2022-08-11 04:25 | 1.5 | O/C | 11kV Maimalari feeder was tried and stayed after conducted Tree Trimmiing | YES | 2022-08-11 13:04 |  | 8:39 | 0.54062 |  |  | No
11KV LIMAWA | TL |  |  | 2022-08-11 05:11 | 0.5 | O/C & E/F | 11kV Limawa feeder was tried and stayed after Tree trimming was conducted along the line. TE Dutse approved. | YES | 2022-08-11 10:30 |  | 5:19 | 0.11076 |  |  | No
11KV KOFAR MARUSA | TL |  |  | 2022-08-11 06:50 | 2.7 | E/F | NOTHING FOUOND | NO | 2022-08-11 20:07 |  | 13:17 | 1.4944 |  |  | No
11KV KANO ROAD | TL |  |  | 2022-08-11 06:52 | 2.9 | E/F | 11kV Kano Road feeder was tried and stayed after amended 1no J&P R phase at Farin Masallaci 500kVA S/S. TE KT City approved. | YES | 2022-08-11 10:40 |  | 3:48 | 0.45917 |  |  | Yes
11KV LAMIDO | TL |  |  | 2022-08-11 06:50 |  | E/F | NOTHING FOUOND | NO | 2022-08-11 11:55 |  | 5:05 | 0 |  |  | No
33KV SMALL SCALE | TL |  |  | 2022-08-11 06:30 | 0.5 | E/F |  |  |  |  | -44784.2708 | -22392.1354 |  |  | No
11KV DUTSIN SAFE | TL |  |  | 2022-08-11 07:52 | 2.7 | O/C & E/F | 11kV D/Safe feeder was tried & stayed okay, cut jumper amended at Dan - Hukku 500kVA S/S. TE KT City approved. | YES | 2022-08-11 11:15 |  | 3:23 | 0.38063 |  |  | #N/A
11KV KANTI | TL |  |  | 2022-08-11 06:10 | 1.2 | E/F |  |  |  |  | -44784.2569 | -53741.1083 |  |  | No
33KV GANO | TL |  |  | 2022-08-11 07:08 | 6.8 | E/F | POLAC OPENED | YES | 2022-08-11 13:20 |  | 6:12 | 1.7567 |  |  | No
11KV NAKOWA | TL |  |  | 2022-08-11 07:18 | 3.3 | E/F |  |  |  |  | -44784.3042 | -147788.2037 |  |  | No
33KV TEXTILE | TL |  |  | 2022-08-11 07:21 | 6.2 | E/F |  |  |  |  | -44784.3063 | -277662.6988 |  |  | No
11KV MOHD DIKKO | TL |  |  | 2022-08-11 08:20 | 3.1 | E/F | 11kV M/Dikko feeder was tried and stayed after isolated Ruffaka 500kVA S/S due to punctured Y Phase XLPE Cable. TE City approved. | YES | 2022-08-11 10:47 |  | 2:27 | 0.31646 |  |  | #N/A
11KV YANKABA | TL |  |  | 2022-08-11 09:34 |  | O/C & E/F | @1427hr 11kV Yankaba feeder was tried and stayed after discovered Indugu 500kVA S/S isolate its self. TE Kawaji approved. | YES | 2022-08-11 14:27 |  | 4:53 | 0 |  |  | No
11KV TARAUNI | TL |  |  | 2022-08-11 09:34 |  | E/F | 11kV Tarauni feeder was tried and stayed after amended B phase Pull out Conductor at Maiduguri Road. TE Hotoro approved. | YES | 2022-08-11 13:05 |  | 3:31 | 0 |  |  | Yes
33KV AJIWA WATER WORKS | TL |  |  | 2022-08-11 08:38 | 0.4 | E/F | 33kV Ajiwa feeder was tried & stayed okay, twisted conductors were separated at CBN junction. RE KTN approved. | YES | 2028-08-11 11:28 |  | 2192.1181 | 876.8472 |  |  | No
11KV DR BALA | TL |  |  | 2022-08-11 09:30 |  | E/F | Treetrimming conducted at Iyaka road | YES | 2022-08-11 19:29 |  | 9:59 | 0 |  |  | No
33KV CBN | TL |  |  | 2022-08-11 09:49 | 5 | E/F | after re-opened of Aliyu Bin Abi Talib isolator nothing found. RE KNC approved. | YES | 2022-08-11 10:03 |  | 0:14 | 0.048611 |  |  | Yes
33KV FALGORE | TL |  |  | 2022-08-11 10:12 | 0.6 | E/F | 33kV Falgore feeder was tried and stayed after opened Kwanar T/Wada. RE Dangora approved. | NO | 2022-08-11 12:41 |  | 2:29 | 0.062083 |  |  | Yes
11KV JAEN | TL |  |  | 2022-08-11 10:15 |  | O/C | AFTER BY PASS B PHASE LIGHTING ARRESTOR AT G/MAIGARI 500KVA S/S | YES | 2022-08-11 17:34 |  | 7:19 | 0 |  |  | No
11KV MUNDADU | TL |  |  | 2022-08-11 10:16 |  | O/C | Blue phase cut jumper was amended at Bubbugaje | NO | 2022-08-11 19:24 |  | 9:08 | 0 |  |  | No
33KV IDH | SE |  |  | 2022-08-11 10:19 | 15.5 |  | 33kV IDH feeder was opened on emergency with 15.5MW due to Airport Road/ Pounded Yam isolator on fire. TE S/Gari reported and RE S/Gari was informed. 33kV IDH feeder was restored okay, R-Phase cut jumper was amended at Pounded Yam junction. RE S/Gari approved. | YES | 2022-08-11 11:43 |  | 1:24 | 0.90417 |  |  | Yes
11KV TALAMIZ | PM | 2022-08-11 10:00 | 2022-08-11 18:00 | 2022-08-11 10:14 |  |  | S.G no 59834 was issued to Safiyanu Ibrahim on 11KV Talamiz feeder for line trace along the line. Duration ( 1000hrs - 1700hrs ). |  | 2022-08-11 16:25 |  | 6:11 | 0
11KV HOUSING ESTATE | PM | 2022-08-11 10:00 | 2022-08-11 17:00 | 2022-08-11 10:40 | 3.6 |  | S.G no 1256 was issued to Jibril Yau Dantsakuwa on 11KV H/Estate feeder with 3.6MW for line trace along the line. Duration ( 1000hrs - 1800hrs ). |  |  |  | -44784.4444 | -161224
33KV ZARIA ROAD | TL |  |  | 2022-08-11 09:49 | 12 | E/F | NOTHING FOUND | NO | 2022-08-11 10:43 |  | 0:54 | 0.45 |  |  | Yes
11KV HOTORO | TL |  |  | 2022-08-11 10:50 |  | O/C & E/F | Sani Marshal 200KVA R-Phase J&P Replaced | YES | 2022-08-11 20:50 |  | 10:00 | 0 |  |  | No
33KV ZARIA ROAD | TL |  |  | 2022-08-11 10:50 | 11 | O/C & E/F | ISOLATED 11KV HOTORO FEEDER FOR LINE PATROLL | YES | 2022-08-11 11:24 |  | 0:34 | 0.25972 |  |  | Yes
11KV N.N.D.C. | PM | 2022-08-11 10:00 | 2022-08-11 13:00 | 2022-08-11 10:41 | 3.6 |  | S.G no 1257 was issued to Jibril Yau Dantsakuwa on 11KV NNDC feeder with 3.6MW for line trace along the line. Duration ( 1000hrs - 1300hrs ). |  | 2022-08-11 15:10 |  | 4:29 | 0.6725
11KV ORTHOPAEDIC | TL |  |  | 2022-08-11 10:38 |  | E/F | REPOSITION R PHASE PULL OUT CONDUCTOR BEHIND SHEIKH ISYAKA RABIU RESIDENT | YES | 2022-08-11 16:51 |  | 6:13 | 0 |  |  | No
11KV TOKARAWA | TL |  |  | 2022-08-11 11:24 |  | NO RI | TREE TRIMMING AT VIVA JUNCTION | YES | 2022-08-11 16:50 |  | 5:26 | 0 |  |  | No
11KV TUDUN WADA | TL |  |  | 2022-08-11 10:55 |  | O/C | 11kV T/Wada feeder was tried and stayed after discovered Hajia kulu 500kVA S/S isolate its self. TE Bompai approved. | YES | 2022-08-11 12:25 |  | 1:30 | 0 |  |  | Yes
11KV YANKABA | PM | 2022-08-11 10:00 | 2022-08-11 13:00 | 2022-08-11 10:50 |  |  | @1050hrs S.G no 51290 was issued to Abdullahi Abdulaziz on 11KV Yankaba feeder for line trace along the line. Duration ( 1000hrs - 1300hrs ). |  | 2022-08-11 14:19 |  | 3:29 | 0
33KV DAWANAU | TL |  |  | 2022-08-11 10:56 | 0.7 | O/C & E/F |  |  |  |  | -44784.4556 | -31349.1189 |  |  | No
33KV KURNA | TL |  |  | 2022-08-11 11:24 | 2.2 | O/C & E/F | ISOLATED DAWANAU FOR LINE PATROLL | YES | 2022-08-11 11:24 |  | 0:00 | 0 |  |  | No
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-11 05:04 | 3.8 | O/C & E/F | NOTHING FOUND | YES | 2022-08-11 11:06 |  | 6:02 | 0.95528 |  |  | #N/A
33KV GASKIYA | TL |  |  | 2022-08-11 11:29 | 7 | O/C & E/F |  |  |  |  | -44784.4785 | -313491.3493 |  |  | No
33KV BUK | TL |  |  | 2022-08-11 11:42 | 12.8 | O/C & E/F | 33kV BUK feeder was tried and stayed after replaced Female contact of K/Famfo isolator. RE Kabuga approved. | NO | 2022-08-11 13:46 |  | 2:04 | 1.1022 |  |  | Yes
11KV MAJE | TL |  |  | 2022-08-11 11:18 | 3 | E/F | TREE BRANCH REMOVED AONG THER LINE | YES | 2022-08-11 12:18 |  | 1:00 | 0.125 | #VALUE! | #VALUE! | Yes
33KV WUDIL | TL |  |  | 2022-08-11 11:31 | 1.8 | E/F | Y PHASE PULL OUT CONDUCTOR FROM CT AMENDED | YES | 2022-08-11 16:01 |  | 4:30 | 0.3375 | #VALUE! | #VALUE! | Yes
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-11 12:16 |  | O/C | TRANSIENT | TRANSIENT | 2022-08-11 12:25 |  | 0:09 | 0 | #VALUE! | #VALUE! | #N/A
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-11 11:41 | 1 | E/F | 33KV DR JAMIL ISOLATED FOR LINE CONTROL | YES | 2022-08-11 12:15 |  | 0:34 | 0.023611 | #VALUE! | #VALUE! | #N/A
33KV BAGAUDA | PM | 2022-08-11 10:00 | 2022-08-11 16:00 | 2022-08-11 11:50 | 0.6 |  | S.G no 15904 was issued to Abdullahi Bello on 33kV Bagauda feeder with 0.6MW for line trace along the line. Duration ( 1000hrs - 1600hrs ). |  | 2022-08-11 17:02 |  | 5:12 | 0.13 | #VALUE! | #VALUE!
33KV BIRNIN KUDU | TL |  |  | 2022-08-11 12:13 | 1.1 | no | 33kV B/Kudu feeder was tried and stayed after opened Round About isolator. RE JGS approved. | yes | 2022-08-11 14:21 |  | 2:08 | 0.097778 | #VALUE! | #VALUE! | Yes
33KV TAMBURAWA W/WORKS | TL |  |  | 2022-08-11 12:21 | 1.2 | O/C & E/F | 33KV DR JAMIL FEEDER ISOLATED FOR LINE PATROL | YES | 2022-08-11 15:46 |  | 3:25 | 0.17083 | #VALUE! | #VALUE! | #N/A
33KV DR. JAMIL GWAMNA | TL |  |  | 2022-08-11 12:21 |  |  | 33kV Dr. Jamil feeder was tried & stayed okay, R-Phase J&P was amended at 7-Up 2.5MVA S/S. RE Panshekara approved. | YES | 2022-08-11 16:08 |  | 3:47 | 0 | #VALUE! | #VALUE! | #N/A
11KV AJASA | SE |  |  | 2022-08-11 12:00 | 1.4 |  | 11kV Ajasa feeder was opened on emergency, discrepancy observed on Y - 0, while R&B - 1.4MW. It was restored on amending a Y-Phase cut jumper on the 1st upriser. TE Zoo Road approved. | YES | 2022-08-11 12:23 |  | 0:23 | 0.022361 | #VALUE! | #VALUE! | Yes
11KV KOFAR NASSARAWA | TL |  |  | 2022-08-11 11:05 | 4.5 | O/C & E/F | tree trimming was conducted | NO | 2022-08-11 20:34 |  | 9:29 | 1.7781 | #VALUE! | #VALUE! | No
33KV CBN | TL |  |  | 2022-08-11 12:38 | 3 | O/C | TRANSIENT | NO | 2022-08-11 12:48 |  | 0:10 | 0.020833 | #VALUE! | #VALUE! | Yes
11KV BELLO DANDAGO | TL |  |  | 2022-08-11 12:48 | 0.03 | O/C & E/F | STAR TIMES 100KVA S/S ISOLATE ITSELF | YES | 2022-08-11 17:06 |  | 4:18 | 0.005375 | #VALUE! | #VALUE! | No
33KV IDH | TL |  |  | 2022-08-11 12:45 | 16 | O/C & E/F | NOTHING FOUND | NO | 2022-08-11 14:56 |  | 2:11 | 1.4556 | #VALUE! | #VALUE! | Yes
33KV MTN | TL |  |  | 2022-08-11 14:39 | 16 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 14:55 |  | 0:16 | 0.17778 | #VALUE! | #VALUE! | Yes
33KV JAHUN | TL |  |  | 2022-08-11 14:42 | 0.7 | E/F |  |  |  |  | -44784.6125 | -31349.2287 | #VALUE! | #VALUE! | No
33KV CHALAWA W/WORKS | TL |  |  | 2022-08-11 14:55 | 3.7 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 15:05 |  | 0:10 | 0.025694 | #VALUE! | #VALUE! | #N/A
33KV CBN | TL |  |  | 8/11/ 22 15:12 | 7 | O/C & E/F | Halliru Akilu isolator was opened | NO | 2022-08-11 19:21 |  | -88.8271 | -621.7896 | #VALUE! | #VALUE! | No
11KV U/UKU | TL |  |  | 2022-08-11 15:48 | 3.5 | O/C & E/F | Branch of tree removed at New Royal 500KVA S/S | YES | 2022-08-11 20:50 |  | 5:02 | 0.73403 | #VALUE! | #VALUE! | #N/A
33KV ZARIA ROAD | TL |  |  | 2022-08-11 15:48 | 17.1 | O/C | ISOLATED U/UKU FOR LINE PATROL | YES | 2022-08-11 15:57 |  | 0:09 | 0.10687 | #VALUE! | #VALUE! | Yes
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-11 16:22 | 15.5 | E/F | HAWAN DAWAKI ISOLATOR OPENED | NO | 2022-08-11 17:30 |  | 1:08 | 0.73194 | #VALUE! | #VALUE! | Yes
11KV INDEPENDENCE | TL |  |  | 2022-08-11 16:35 | 1.2 | O/C | Suspected MAGANDA RD Tee-off was isolated affecting 4no DTs | YES | 2022-08-11 20:06 |  | 3:31 | 0.17583 | #VALUE! | #VALUE! | Yes
11KV KARKASARA | TL |  |  | 2022-08-11 17:03 | 4.5 | O/C & E/F | Branch of tree removed at tudun fulani | YES | 87/11/22 20:42 |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
33KV ZARIA ROAD | TL |  |  | 2022-08-11 17:03 | 17.5 | O/C | ISOLATED KARKASARA | YES | 2022-08-11 17:13 |  | 0:10 | 0.12153 | #VALUE! | #VALUE! | Yes
33KV NNPC | TL |  |  | 2022-08-11 17:10 | 3 | O/C & E/F | RE-OPENED JOGANA ISOLATOR | NO | 2022-08-11 17:27 |  | 0:17 | 0.035417 | #VALUE! | #VALUE! | Yes
33KV GASKIYA | TL |  |  | 2022-08-11 17:34 | 9 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 17:51 |  | 0:17 | 0.10625 | #VALUE! | #VALUE! | Yes
33KV GASKIYA | TL |  |  | 2022-08-11 17:34 | 9 | O/C | TRANSIENT |  |  |  | -44784.7319 | -403062.5875 | #VALUE! | #VALUE! | No
11KV AHMADU BELLO | TL |  |  | 2022-08-11 17:50 | 3.2 | E/F | Bird bridge the line at Dankabo Closed | YES | 2022-08-11 18:24 |  | 0:34 | 0.075556 | #VALUE! | #VALUE! | Yes
33KV IDH | SE |  |  | 2022-08-11 18:26 | 12.5 |  | Due to arching on Flying Training Sch. isolator |  | 2022-08-11 18:40 |  | 0:14 | 0.12153 | #VALUE! | #VALUE! | Yes
33KV ZARIA ROAD | TL |  |  | 2022-08-11 18:57 | 12 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 19:12 |  | 0:15 | 0.125 | #VALUE! | #VALUE! | Yes
11KV GWAMMAJA | SE |  |  | 2022-08-11 19:18 | 2.2 |  | Due to masaka 500KVA S/staion on fire | YES | 2022-08-11 20:40 |  | 1:22 | 0.12528 | #VALUE! | #VALUE! | Yes
33KV RIJIYAR ZAKI | TL |  |  | 2022-08-11 19:14 | 15.6 | E/F | Hawan Dawaki isolator was isolated | NO | 2022-08-11 20:34 |  | 1:20 | 0.86667 | #VALUE! | #VALUE! | Yes
33KV GANO | TL |  |  | 2022-08-11 19:18 | 6 | E/F | POLAC isolator was opened | NO | 2022-08-11 20:17 |  | 0:59 | 0.24583 | #VALUE! | #VALUE! | Yes
33KV MUSAWA | TL |  |  | 2022-08-11 19:25 | 5.5 | E/F | OPENED MUSAWA LEG | NO | 2022-08-12 09:01 |  | 13:36 | 3.1167 | #VALUE! | #VALUE! | No
33KV BIRNIN KUDU | TL |  |  | 2022-08-11 19:33 | 5.1 |  | Danmasara isolator was opened | NO | 2022-08-11 21:08 |  | 1:35 | 0.33646 | #VALUE! | #VALUE! | Yes
33KV SUMAILA | TL |  |  | 2022-08-11 19:37 | 2.2 |  | Rungumau isolator was opened | NO | 2022-08-11 21:08 |  | 1:31 | 0.13903 | #VALUE! | #VALUE! | Yes
33KV IDH | TL |  |  | 2022-08-11 19:57 | 10 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 20:07 |  | 0:10 | 0.069444 | #VALUE! | #VALUE! | Yes
33KV GANO | TL |  |  | 2022-08-11 21:07 | 0.5 | [5 empty] | -44784.8799 | -22392.4399 | #VALUE! | #VALUE! | No
33KV WUDIL | TL |  |  | 2022-08-11 21:07 | 1.5 | E/F | TRANSIENT | TRANSIENT | 2022-08-11 21:18 |  | 0:11 | 0.011458 | #VALUE! | #VALUE! | Yes
33KV KARAYE | TL |  |  | 2022-08-11 20:18 | 3.6 | E/F | Dangora isolator was opened | NO | 2022-08-11 21:37 |  | 1:19 | 0.1975 | #VALUE! | #VALUE! | Yes
11KV KARKASARA | TL |  |  | 2022-08-11 22:45 | 4.7 | O/C & E/F | Tree trimming was conducted at Raihan street | NO | 2022-08-12 01:19 |  | 2:34 | 0.50264 | #VALUE! | #VALUE! | Yes
33KV GARKO | TL |  |  | 2022-08-11 22:21 | 2.2 | [5 empty] | -44784.9313 | -98526.8488 | #VALUE! | #VALUE! | No
33KV ZARIA ROAD | TL |  |  | 2022-08-11 23:25 | 15.2 | O/C | TRANSIENT | TRANSIENT | 2022-08-11 23:35 |  | 0:10 | 0.10556 | #VALUE! | #VALUE! | Yes
11KV TARAUNI | SE |  |  | 2022-08-11 23:35 | 2 |  | Due to the hot spotobserved on Red phase bold and nut clamp on 33KV CBN Isolator at 132/33KV dAN AGUNDI TS |  |  |  | -44784.9826 | -89569.9653 | #VALUE! | #VALUE! | No

## 12
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 13
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 14
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 15
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 16
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 17
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 18
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 19
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 20
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 21
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 22
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0 |  |  |  | ABDULLAHI ABUBAKAR
[11 empty] | 0:00 | 0 |  |  |  | USMAN SA'ADU
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
Note on J3: Author: OUTAGE WAS GRANTED ON THE FEEDER BETWEEN 1013HRS TO 1813HRS OF THE DAY. HENCE THE DOWNTIME.

## 23
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 24
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 25
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0 |  |  |  |  | ,
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 26
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 27
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 28
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 29
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 30
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0

## 31
Name of Feeder | Fault Type | Approved Outage Time | Approved Restoration Time | Tripping Date & Time (MM/DD/YY) | Load Interrupted (MW) | Relay Indication | Brief Description | Any Discovery On Patrols? | Restoration Date & Time (MM/DD/YY) | Load at the time of Restoration (MW) | Outage Duration | Total Energy Loss (MWH) | Outage Surrender within duration | Extended Time | Fault Cleared in Specified Time | Name & Designation of Permit Holder
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0
[11 empty] | 0:00 | 0